## Overall Report Summary
Item | Value
Report for File: | school_1.csv
Station Name: | CliftonSchool_1
Station IP: | UnknownIP
Export Date: | UnknownDate
Total Devices Found: | 22
Device Count per Trunk:
Trunk | Device Count
MstpTrunk1 | 3
MstpTrunk2 | 18
MstpTrunk3 | 1

## Device List Details
Type | Network | Trunk | Device | Address | DeviceType | PointFolder | PointName | PointType | Value | Status
Device | BacnetNetwork | MstpTrunk1 | RTU1_Cafe | 1000:15 | device:100021 config
Device | BacnetNetwork | MstpTrunk1 | RTU2_Gym | 1000:16 | device:100022 config
Device | BacnetNetwork | MstpTrunk1 | RTU3_Gym | 1000:17 | device:100023 config
Device | BacnetNetwork | MstpTrunk2 | UV_RM101 | 2000:0f | device:200015 config
Device | BacnetNetwork | MstpTrunk2 | UV_RM102 | 2000:0e | device:200014 config
Device | BacnetNetwork | MstpTrunk2 | UV_RM103 | 2000:10 | device:200016 config
Device | BacnetNetwork | MstpTrunk2 | UV_RM104 | 2000:0d | device:200013 config
Device | BacnetNetwork | MstpTrunk2 | UV_RM105 | 2000:11 | device:200017 config
Device | BacnetNetwork | MstpTrunk2 | UV_RM106 | 2000:0c | device:200012 config
Device | BacnetNetwork | MstpTrunk2 | UV_RM107 | 2000:12 | device:200018 config
Device | BacnetNetwork | MstpTrunk2 | UV_RM108 | 2000:0b | device:200011 config
Device | BacnetNetwork | MstpTrunk2 | UV_201_EF9 | 2000:04 | device:20004 config
Device | BacnetNetwork | MstpTrunk2 | UV_202_EF8 | 2000:05 | device:20005 config
Device | BacnetNetwork | MstpTrunk2 | UV_RM203 | 2000:03 | device:20003 config
Device | BacnetNetwork | MstpTrunk2 | UV_RM204 | 2000:06 | device:20006 config
Device | BacnetNetwork | MstpTrunk2 | UV_RM205 | 2000:02 | device:20002 config
Device | BacnetNetwork | MstpTrunk2 | UV_206_EF7 | 2000:07 | device:20007 config
Device | BacnetNetwork | MstpTrunk2 | UV_207_EF10 | 2000:01 | device:20001 config
Device | BacnetNetwork | MstpTrunk2 | UV_RM208 | 2000:08 | device:20008 config
Device | BacnetNetwork | MstpTrunk2 | EF4_3_Bathrooms | 2000:14 | device:200020 config
Device | BacnetNetwork | MstpTrunk2 | CH_FTR | 2000:18 | device:200024 config
Device | BacnetNetwork | MstpTrunk3 | DAIKIN DBACS | 1:192.168.1.141:47808 | device:3000 config

## RTU1_Cafe
Type | Network | Trunk | Device | Address | DeviceType | PointFolder | PointName | PointType | Value | Status
Point | BacnetNetwork | MstpTrunk1 | RTU1_Cafe |  |  | Inputs | SpaceTemp | control:NumericPoint | 68.54 {ok}
Point | BacnetNetwork | MstpTrunk1 | RTU1_Cafe |  |  | Inputs | SpaceCO2 | control:NumericPoint | 391.20 {ok}
Point | BacnetNetwork | MstpTrunk1 | RTU1_Cafe |  |  | Inputs | RATemp | control:NumericPoint | 65.66 {ok}
Point | BacnetNetwork | MstpTrunk1 | RTU1_Cafe |  |  | Inputs | SpaceRH | control:NumericPoint | 30.87 {ok}
Point | BacnetNetwork | MstpTrunk1 | RTU1_Cafe |  |  | Inputs | DischAirTemp | control:NumericPoint | 64.37 {ok}
Point | BacnetNetwork | MstpTrunk1 | RTU1_Cafe |  |  | Inputs | OutdoorTemp | control:NumericPoint | 58.91 {ok}
Point | BacnetNetwork | MstpTrunk1 | RTU1_Cafe |  |  | Inputs | DischLn1Temp | control:NumericPoint | 81.05 {ok}
Point | BacnetNetwork | MstpTrunk1 | RTU1_Cafe |  |  | Inputs | SucnRefTemp | control:NumericPoint | 80.10 {ok}
Point | BacnetNetwork | MstpTrunk1 | RTU1_Cafe |  |  | Inputs | RefSuctionP | control:NumericPoint | 151.36 {ok}
Point | BacnetNetwork | MstpTrunk1 | RTU1_Cafe |  |  | Inputs | EFT_LCT | control:NumericPoint | 64.47 {ok}
Point | BacnetNetwork | MstpTrunk1 | RTU1_Cafe |  |  | Inputs | BldgStatPress | control:NumericPoint | -0.01 {ok}
Point | BacnetNetwork | MstpTrunk1 | RTU1_Cafe |  |  | Inputs | ERWheelSpd | control:NumericPoint | 0.00 {ok}
Point | BacnetNetwork | MstpTrunk1 | RTU1_Cafe |  |  | Inputs | ERLAT | control:NumericPoint | 57.75 {ok}
Point | BacnetNetwork | MstpTrunk1 | RTU1_Cafe |  |  | Inputs | EREAT | control:NumericPoint | 56.81 {ok}
Point | BacnetNetwork | MstpTrunk1 | RTU1_Cafe |  |  | Inputs | FanSpd | control:NumericPoint | 60.00 {ok}
Point | BacnetNetwork | MstpTrunk1 | RTU1_Cafe |  |  | Inputs | EconCapacity | control:NumericPoint | 30.00 {ok}
Point | BacnetNetwork | MstpTrunk1 | RTU1_Cafe |  |  | Inputs | HtgCapacity | control:NumericPoint | 0.00 {ok}
Point | BacnetNetwork | MstpTrunk1 | RTU1_Cafe |  |  | Inputs | ClgCapacity | control:NumericPoint | 0.00 {ok}
Point | BacnetNetwork | MstpTrunk1 | RTU1_Cafe |  |  | Inputs | SpaceDewPt | control:NumericPoint | 34.09 {ok}
Point | BacnetNetwork | MstpTrunk1 | RTU1_Cafe |  |  | Inputs | RefDischP | control:NumericPoint | 168.52 {ok}
Point | BacnetNetwork | MstpTrunk1 | RTU1_Cafe |  |  | Inputs | ExpValveProb | control:BooleanPoint | false {ok}
Point | BacnetNetwork | MstpTrunk1 | RTU1_Cafe |  |  | Inputs | HiPress1Prb | control:BooleanPoint | false {ok}
Point | BacnetNetwork | MstpTrunk1 | RTU1_Cafe |  |  | Inputs | ChargeLossPrb | control:BooleanPoint | false {ok}
Point | BacnetNetwork | MstpTrunk1 | RTU1_Cafe |  |  | Inputs | LoPress1Prb | control:BooleanPoint | false {ok}
Point | BacnetNetwork | MstpTrunk1 | RTU1_Cafe |  |  | Inputs | LoChargePrb | control:BooleanPoint | false {ok}
Point | BacnetNetwork | MstpTrunk1 | RTU1_Cafe |  |  | Inputs | HiDLTempPrb | control:BooleanPoint | false {ok}
Point | BacnetNetwork | MstpTrunk1 | RTU1_Cafe |  |  | Inputs | INVCompPrb | control:BooleanPoint | false {ok}
Point | BacnetNetwork | MstpTrunk1 | RTU1_Cafe |  |  | Inputs | OAFanPrb | control:BooleanPoint | false {ok}
Point | BacnetNetwork | MstpTrunk1 | RTU1_Cafe |  |  | Inputs | LoPressDiffPrb | control:BooleanPoint | false {ok}
Point | BacnetNetwork | MstpTrunk1 | RTU1_Cafe |  |  | Inputs | ExhFanState | control:BooleanPoint | true {ok}
Point | BacnetNetwork | MstpTrunk1 | RTU1_Cafe |  |  | Inputs | DirtyFilterSw | control:BooleanPoint | ""true {alarm | unackedAlarm}""
Point | BacnetNetwork | MstpTrunk1 | RTU1_Cafe |  |  | Inputs | HiPress1Sw | control:BooleanPoint | true {ok}
Point | BacnetNetwork | MstpTrunk1 | RTU1_Cafe |  |  | Inputs | AirFlwSw | control:BooleanPoint | true {ok}
Point | BacnetNetwork | MstpTrunk1 | RTU1_Cafe |  |  | Inputs | Ret.ExhFanWrn | control:BooleanPoint | false {ok}
Point | BacnetNetwork | MstpTrunk1 | RTU1_Cafe |  |  | Inputs | DuctHiLmtSw | control:BooleanPoint | true {ok}
Point | BacnetNetwork | MstpTrunk1 | RTU1_Cafe |  |  | Inputs | EmergencyOffSw | control:BooleanPoint | true {ok}
Point | BacnetNetwork | MstpTrunk1 | RTU1_Cafe |  |  | Inputs | ReheatCapacity | control:NumericPoint | 0.00 {ok}
Point | BacnetNetwork | MstpTrunk1 | RTU1_Cafe |  |  | Inputs | OAFlow | control:NumericPoint | 121.80 {ok}
Point | BacnetNetwork | MstpTrunk1 | RTU1_Cafe |  |  | SetPoints | UnoccCoolSetpt | control:NumericWritable | 85.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk1 | RTU1_Cafe |  |  | SetPoints | UnoccHeatSetpt | control:NumericWritable | 65.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk1 | RTU1_Cafe |  |  | SetPoints | OccCoolSP | control:NumericWritable | 75.00 {overridden} @ 8
Point | BacnetNetwork | MstpTrunk1 | RTU1_Cafe |  |  | SetPoints | OccHeatSP | control:NumericWritable | 68.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk1 | RTU1_Cafe |  |  | SetPoints | DAClgSetpt | control:NumericWritable | 55.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk1 | RTU1_Cafe |  |  | SetPoints | DefaultDATClgSetpt | control:NumericWritable | 55.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk1 | RTU1_Cafe |  |  | SetPoints | DefaultDATHtgSetpt | control:NumericWritable | 120.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk1 | RTU1_Cafe |  |  | SetPoints | DAHtgSetpt | control:NumericWritable | 100.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk1 | RTU1_Cafe |  |  | SetPoints | HumiditySP | control:NumericWritable | 50.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk1 | RTU1_Cafe |  |  | SetPoints | EmergOverride | control:EnumWritable | Normal {ok} @ def
Point | BacnetNetwork | MstpTrunk1 | RTU1_Cafe |  |  | SetPoints | BldgStaticSP | control:NumericWritable | 0.05 {ok} @ def
Point | BacnetNetwork | MstpTrunk1 | RTU1_Cafe |  |  | SetPoints | DACMWUSpt | control:NumericWritable | 70.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk1 | RTU1_Cafe |  |  | SetPoints | ExhRetFanCtrl | control:EnumWritable | BldgP(2) {ok} @ def
Point | BacnetNetwork | MstpTrunk1 | RTU1_Cafe |  |  | SetPoints | MinDehumLCTSpt | control:NumericWritable | 52.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk1 | RTU1_Cafe |  |  | SetPoints | EffDATempSP | control:NumericPoint | 55.00 {ok}
Point | BacnetNetwork | MstpTrunk1 | RTU1_Cafe |  |  | SetPoints | DewpointSP | control:NumericWritable | 50.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk1 | RTU1_Cafe |  |  | SetPoints | CtrlTempScr | control:EnumWritable | Space {ok} @ def
Point | BacnetNetwork | MstpTrunk1 | RTU1_Cafe |  |  | SetPoints | SupFanCtrl | control:EnumWritable | 1ZnVAV {ok} @ def
Point | BacnetNetwork | MstpTrunk1 | RTU1_Cafe |  |  | Monitor | ActiveFault | control:NumericPoint | 0.00 {ok}
Point | BacnetNetwork | MstpTrunk1 | RTU1_Cafe |  |  | Monitor | ActiveProblem | control:NumericPoint | 0.00 {ok}
Point | BacnetNetwork | MstpTrunk1 | RTU1_Cafe |  |  | Monitor | ActiveWarning | control:NumericPoint | 0.00 {ok}
Point | BacnetNetwork | MstpTrunk1 | RTU1_Cafe |  |  | Monitor | AlarmValue | control:NumericPoint | 0.00 {ok}
Point | BacnetNetwork | MstpTrunk1 | RTU1_Cafe |  |  | Monitor | UnitState | control:EnumPoint | FanOnly {ok}
Point | BacnetNetwork | MstpTrunk1 | RTU1_Cafe |  |  | Monitor | MWUStatus | control:EnumPoint | Inactive {ok}
Point | BacnetNetwork | MstpTrunk1 | RTU1_Cafe |  |  | Monitor | ClgStatus | control:EnumPoint | Enabled {ok}
Point | BacnetNetwork | MstpTrunk1 | RTU1_Cafe |  |  | Monitor | EconoStatus | control:EnumPoint | Enabled {ok}
Point | BacnetNetwork | MstpTrunk1 | RTU1_Cafe |  |  | Monitor | HtgStatus | control:EnumPoint | OffAmb {ok}
Point | BacnetNetwork | MstpTrunk1 | RTU1_Cafe |  |  | Monitor | EffectOccup | control:EnumPoint | Occ {ok}
Point | BacnetNetwork | MstpTrunk1 | RTU1_Cafe |  |  | Monitor | McQuayStatus | control:EnumPoint | Enabled {ok}
Point | BacnetNetwork | MstpTrunk1 | RTU1_Cafe |  |  | Monitor | ERWhlOnOff | control:EnumWritable | Off {ok} @ def
Point | BacnetNetwork | MstpTrunk1 | RTU1_Cafe |  |  | Monitor | ClearAlarms | control:EnumWritable | No {ok} @ def
Point | BacnetNetwork | MstpTrunk1 | RTU1_Cafe |  |  | Monitor | UseTstatSpts | control:EnumWritable | No {ok} @ def
Point | BacnetNetwork | MstpTrunk1 | RTU1_Cafe |  |  | Monitor | DehumStatus | control:EnumPoint | Disable {ok}
Point | BacnetNetwork | MstpTrunk1 | RTU1_Cafe |  |  | Monitor | ApplicCmd | control:EnumWritable | Auto {ok} @ def
Point | BacnetNetwork | MstpTrunk1 | RTU1_Cafe |  |  | Monitor | DemandShed | control:EnumWritable | Auto {ok} @ def
Point | BacnetNetwork | MstpTrunk1 | RTU1_Cafe |  |  | Schedule | OccManCmd | control:EnumWritable | Occ {ok} @ 16
Point | BacnetNetwork | MstpTrunk1 | RTU1_Cafe |  |  | Schedule | SetReset | kitControl:BqlExprComponent | false | {ok}
Point | BacnetNetwork | MstpTrunk1 | RTU1_Cafe |  |  | Schedule | RTU1_OptStartStop | vykonPro:OptStartStop | N/A

## RTU2_Gym
Type | Network | Trunk | Device | Address | DeviceType | PointFolder | PointName | PointType | Value | Status
Point | BacnetNetwork | MstpTrunk1 | RTU2_Gym |  |  | Inputs | SpaceTemp | control:NumericPoint | 71.27 {ok}
Point | BacnetNetwork | MstpTrunk1 | RTU2_Gym |  |  | Inputs | SpaceCO2 | control:NumericPoint | 394.40 {ok}
Point | BacnetNetwork | MstpTrunk1 | RTU2_Gym |  |  | Inputs | RATemp | control:NumericPoint | 71.23 {ok}
Point | BacnetNetwork | MstpTrunk1 | RTU2_Gym |  |  | Inputs | SpaceRH | control:NumericPoint | 28.80 {ok}
Point | BacnetNetwork | MstpTrunk1 | RTU2_Gym |  |  | Inputs | DischAirTemp | control:NumericPoint | 67.66 {ok}
Point | BacnetNetwork | MstpTrunk1 | RTU2_Gym |  |  | Inputs | OutdoorTemp | control:NumericPoint | 56.93 {ok}
Point | BacnetNetwork | MstpTrunk1 | RTU2_Gym |  |  | Inputs | DischLn1Temp | control:NumericPoint | 81.58 {ok}
Point | BacnetNetwork | MstpTrunk1 | RTU2_Gym |  |  | Inputs | SucnRefTemp | control:NumericPoint | 82.15 {ok}
Point | BacnetNetwork | MstpTrunk1 | RTU2_Gym |  |  | Inputs | RefSuctionP | control:NumericPoint | 99.57 {ok}
Point | BacnetNetwork | MstpTrunk1 | RTU2_Gym |  |  | Inputs | EFT_LCT | control:NumericPoint | 64.79 {ok}
Point | BacnetNetwork | MstpTrunk1 | RTU2_Gym |  |  | Inputs | BldgStatPress | control:NumericPoint | -0.01 {ok}
Point | BacnetNetwork | MstpTrunk1 | RTU2_Gym |  |  | Inputs | ERWheelSpd | control:NumericPoint | 0.00 {ok}
Point | BacnetNetwork | MstpTrunk1 | RTU2_Gym |  |  | Inputs | ERLAT | control:NumericPoint | 57.65 {ok}
Point | BacnetNetwork | MstpTrunk1 | RTU2_Gym |  |  | Inputs | EREAT | control:NumericPoint | 56.94 {ok}
Point | BacnetNetwork | MstpTrunk1 | RTU2_Gym |  |  | Inputs | FanSpd | control:NumericPoint | 59.00 {ok}
Point | BacnetNetwork | MstpTrunk1 | RTU2_Gym |  |  | Inputs | EconCapacity | control:NumericPoint | 15.19 {ok}
Point | BacnetNetwork | MstpTrunk1 | RTU2_Gym |  |  | Inputs | HtgCapacity | control:NumericPoint | 0.00 {ok}
Point | BacnetNetwork | MstpTrunk1 | RTU2_Gym |  |  | Inputs | ClgCapacity | control:NumericPoint | 0.00 {ok}
Point | BacnetNetwork | MstpTrunk1 | RTU2_Gym |  |  | Inputs | SpaceDewPt | control:NumericPoint | 37.52 {ok}
Point | BacnetNetwork | MstpTrunk1 | RTU2_Gym |  |  | Inputs | RefDischP | control:NumericPoint | 167.82 {ok}
Point | BacnetNetwork | MstpTrunk1 | RTU2_Gym |  |  | Inputs | ExpValveProb | control:BooleanPoint | false {ok}
Point | BacnetNetwork | MstpTrunk1 | RTU2_Gym |  |  | Inputs | HiPress1Prb | control:BooleanPoint | false {ok}
Point | BacnetNetwork | MstpTrunk1 | RTU2_Gym |  |  | Inputs | ChargeLossPrb | control:BooleanPoint | false {ok}
Point | BacnetNetwork | MstpTrunk1 | RTU2_Gym |  |  | Inputs | LoPress1Prb | control:BooleanPoint | false {ok}
Point | BacnetNetwork | MstpTrunk1 | RTU2_Gym |  |  | Inputs | LoChargePrb | control:BooleanPoint | false {ok}
Point | BacnetNetwork | MstpTrunk1 | RTU2_Gym |  |  | Inputs | HiDLTempPrb | control:BooleanPoint | false {ok}
Point | BacnetNetwork | MstpTrunk1 | RTU2_Gym |  |  | Inputs | INVCompPrb | control:BooleanPoint | false {ok}
Point | BacnetNetwork | MstpTrunk1 | RTU2_Gym |  |  | Inputs | OAFanPrb | control:BooleanPoint | false {ok}
Point | BacnetNetwork | MstpTrunk1 | RTU2_Gym |  |  | Inputs | LoPressDiffPrb | control:BooleanPoint | false {ok}
Point | BacnetNetwork | MstpTrunk1 | RTU2_Gym |  |  | Inputs | ExhFanState | control:BooleanPoint | false {ok}
Point | BacnetNetwork | MstpTrunk1 | RTU2_Gym |  |  | Inputs | DirtyFilterSw | control:BooleanPoint | ""true {alarm | unackedAlarm}""
Point | BacnetNetwork | MstpTrunk1 | RTU2_Gym |  |  | Inputs | HiPress1Sw | control:BooleanPoint | true {ok}
Point | BacnetNetwork | MstpTrunk1 | RTU2_Gym |  |  | Inputs | AirFlwSw | control:BooleanPoint | true {ok}
Point | BacnetNetwork | MstpTrunk1 | RTU2_Gym |  |  | Inputs | Ret.ExhFanWrn | control:BooleanPoint | false {ok}
Point | BacnetNetwork | MstpTrunk1 | RTU2_Gym |  |  | Inputs | DuctHiLmtSw | control:BooleanPoint | true {ok}
Point | BacnetNetwork | MstpTrunk1 | RTU2_Gym |  |  | Inputs | EmergencyOffSw | control:BooleanPoint | true {ok}
Point | BacnetNetwork | MstpTrunk1 | RTU2_Gym |  |  | Inputs | ReheatCapacity | control:NumericPoint | 0.00 {ok}
Point | BacnetNetwork | MstpTrunk1 | RTU2_Gym |  |  | Inputs | OAFlow | control:NumericPoint | 115.20 {ok}
Point | BacnetNetwork | MstpTrunk1 | RTU2_Gym |  |  | SetPoints | UnoccCoolSetpt | control:NumericWritable | 85.00 {ok} @ 10
Point | BacnetNetwork | MstpTrunk1 | RTU2_Gym |  |  | SetPoints | UnoccHeatSetpt | control:NumericWritable | 65.00 {ok} @ 10
Point | BacnetNetwork | MstpTrunk1 | RTU2_Gym |  |  | SetPoints | OccCoolSP | control:NumericWritable | 76.00 {overridden} @ 8
Point | BacnetNetwork | MstpTrunk1 | RTU2_Gym |  |  | SetPoints | OccHeatSP | control:NumericWritable | 70.00 {overridden} @ 8
Point | BacnetNetwork | MstpTrunk1 | RTU2_Gym |  |  | SetPoints | DAClgSetpt | control:NumericWritable | 55.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk1 | RTU2_Gym |  |  | SetPoints | DefaultDATClgSetpt | control:NumericWritable | 55.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk1 | RTU2_Gym |  |  | SetPoints | DefaultDATHtgSetpt | control:NumericWritable | 120.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk1 | RTU2_Gym |  |  | SetPoints | DAHtgSetpt | control:NumericWritable | 100.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk1 | RTU2_Gym |  |  | SetPoints | HumiditySP | control:NumericWritable | 50.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk1 | RTU2_Gym |  |  | SetPoints | EmergOverride | control:EnumWritable | Normal {ok} @ def
Point | BacnetNetwork | MstpTrunk1 | RTU2_Gym |  |  | SetPoints | BldgStaticSP | control:NumericWritable | 0.05 {ok} @ def
Point | BacnetNetwork | MstpTrunk1 | RTU2_Gym |  |  | SetPoints | DACMWUSpt | control:NumericWritable | 70.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk1 | RTU2_Gym |  |  | SetPoints | ExhRetFanCtrl | control:EnumWritable | BldgP(2) {ok} @ def
Point | BacnetNetwork | MstpTrunk1 | RTU2_Gym |  |  | SetPoints | MinDehumLCTSpt | control:NumericWritable | 52.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk1 | RTU2_Gym |  |  | SetPoints | EffDATempSP | control:NumericPoint | 54.99 {ok}
Point | BacnetNetwork | MstpTrunk1 | RTU2_Gym |  |  | SetPoints | DewpointSP | control:NumericWritable | 50.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk1 | RTU2_Gym |  |  | SetPoints | CtrlTempScr | control:EnumWritable | Space {ok} @ def
Point | BacnetNetwork | MstpTrunk1 | RTU2_Gym |  |  | SetPoints | SupFanCtrl | control:EnumWritable | 1ZnVAV {ok} @ def
Point | BacnetNetwork | MstpTrunk1 | RTU2_Gym |  |  | Monitor | ActiveFault | control:NumericPoint | 0.00 {ok}
Point | BacnetNetwork | MstpTrunk1 | RTU2_Gym |  |  | Monitor | ActiveProblem | control:NumericPoint | 0.00 {ok}
Point | BacnetNetwork | MstpTrunk1 | RTU2_Gym |  |  | Monitor | ActiveWarning | control:NumericPoint | 0.00 {ok}
Point | BacnetNetwork | MstpTrunk1 | RTU2_Gym |  |  | Monitor | AlarmValue | control:NumericPoint | 0.00 {ok}
Point | BacnetNetwork | MstpTrunk1 | RTU2_Gym |  |  | Monitor | UnitState | control:EnumPoint | FanOnly {ok}
Point | BacnetNetwork | MstpTrunk1 | RTU2_Gym |  |  | Monitor | MWUStatus | control:EnumPoint | Inactive {ok}
Point | BacnetNetwork | MstpTrunk1 | RTU2_Gym |  |  | Monitor | ClgStatus | control:EnumPoint | Enabled {ok}
Point | BacnetNetwork | MstpTrunk1 | RTU2_Gym |  |  | Monitor | EconoStatus | control:EnumPoint | Enabled {ok}
Point | BacnetNetwork | MstpTrunk1 | RTU2_Gym |  |  | Monitor | HtgStatus | control:EnumPoint | Enabled {ok}
Point | BacnetNetwork | MstpTrunk1 | RTU2_Gym |  |  | Monitor | EffectOccup | control:EnumPoint | Occ {ok}
Point | BacnetNetwork | MstpTrunk1 | RTU2_Gym |  |  | Monitor | McQuayStatus | control:EnumPoint | Enabled {ok}
Point | BacnetNetwork | MstpTrunk1 | RTU2_Gym |  |  | Monitor | ERWhlOnOff | control:EnumWritable | Off {ok} @ def
Point | BacnetNetwork | MstpTrunk1 | RTU2_Gym |  |  | Monitor | ClearAlarms | control:EnumWritable | No {ok} @ def
Point | BacnetNetwork | MstpTrunk1 | RTU2_Gym |  |  | Monitor | DehumStatus | control:EnumPoint | Disable {ok}
Point | BacnetNetwork | MstpTrunk1 | RTU2_Gym |  |  | Monitor | UseTstatSpts | control:EnumWritable | No {ok} @ def
Point | BacnetNetwork | MstpTrunk1 | RTU2_Gym |  |  | Monitor | ApplicCmd | control:EnumWritable | Auto {ok} @ def
Point | BacnetNetwork | MstpTrunk1 | RTU2_Gym |  |  | Monitor | DemandShed | control:EnumWritable | Auto {ok} @ def
Point | BacnetNetwork | MstpTrunk1 | RTU2_Gym |  |  | Schedule | OccManCmd | control:EnumWritable | Occ {ok} @ 16
Point | BacnetNetwork | MstpTrunk1 | RTU2_Gym |  |  | Schedule | SetReset | kitControl:BqlExprComponent | false | {ok}
Point | BacnetNetwork | MstpTrunk1 | RTU2_Gym |  |  | Schedule | RTU2_OptStartStop | vykonPro:OptStartStop | N/A

## RTU3_Gym
Type | Network | Trunk | Device | Address | DeviceType | PointFolder | PointName | PointType | Value | Status
Point | BacnetNetwork | MstpTrunk1 | RTU3_Gym |  |  | Inputs | SpaceTemp | control:NumericPoint | 71.35 {ok}
Point | BacnetNetwork | MstpTrunk1 | RTU3_Gym |  |  | Inputs | SpaceCO2 | control:NumericPoint | 399.40 {ok}
Point | BacnetNetwork | MstpTrunk1 | RTU3_Gym |  |  | Inputs | RATemp | control:NumericPoint | 69.30 {ok}
Point | BacnetNetwork | MstpTrunk1 | RTU3_Gym |  |  | Inputs | SpaceRH | control:NumericPoint | 29.21 {ok}
Point | BacnetNetwork | MstpTrunk1 | RTU3_Gym |  |  | Inputs | DischAirTemp | control:NumericPoint | 67.23 {ok}
Point | BacnetNetwork | MstpTrunk1 | RTU3_Gym |  |  | Inputs | OutdoorTemp | control:NumericPoint | 57.28 {ok}
Point | BacnetNetwork | MstpTrunk1 | RTU3_Gym |  |  | Inputs | DischLn1Temp | control:NumericPoint | 79.64 {ok}
Point | BacnetNetwork | MstpTrunk1 | RTU3_Gym |  |  | Inputs | SucnRefTemp | control:NumericPoint | 79.09 {ok}
Point | BacnetNetwork | MstpTrunk1 | RTU3_Gym |  |  | Inputs | RefSuctionP | control:NumericPoint | 91.17 {ok}
Point | BacnetNetwork | MstpTrunk1 | RTU3_Gym |  |  | Inputs | EFT_LCT | control:NumericPoint | 61.57 {ok}
Point | BacnetNetwork | MstpTrunk1 | RTU3_Gym |  |  | Inputs | BldgStatPress | control:NumericPoint | -0.01 {ok}
Point | BacnetNetwork | MstpTrunk1 | RTU3_Gym |  |  | Inputs | ERWheelSpd | control:NumericPoint | 0.00 {ok}
Point | BacnetNetwork | MstpTrunk1 | RTU3_Gym |  |  | Inputs | ERLAT | control:NumericPoint | 57.69 {ok}
Point | BacnetNetwork | MstpTrunk1 | RTU3_Gym |  |  | Inputs | EREAT | control:NumericPoint | 58.15 {ok}
Point | BacnetNetwork | MstpTrunk1 | RTU3_Gym |  |  | Inputs | FanSpd | control:NumericPoint | 60.00 {ok}
Point | BacnetNetwork | MstpTrunk1 | RTU3_Gym |  |  | Inputs | EconCapacity | control:NumericPoint | 15.00 {ok}
Point | BacnetNetwork | MstpTrunk1 | RTU3_Gym |  |  | Inputs | HtgCapacity | control:NumericPoint | 0.00 {ok}
Point | BacnetNetwork | MstpTrunk1 | RTU3_Gym |  |  | Inputs | ClgCapacity | control:NumericPoint | 0.00 {ok}
Point | BacnetNetwork | MstpTrunk1 | RTU3_Gym |  |  | Inputs | SpaceDewPt | control:NumericPoint | 35.68 {ok}
Point | BacnetNetwork | MstpTrunk1 | RTU3_Gym |  |  | Inputs | RefDischP | control:NumericPoint | 165.90 {ok}
Point | BacnetNetwork | MstpTrunk1 | RTU3_Gym |  |  | Inputs | ExpValveProb | control:BooleanPoint | false {ok}
Point | BacnetNetwork | MstpTrunk1 | RTU3_Gym |  |  | Inputs | HiPress1Prb | control:BooleanPoint | false {ok}
Point | BacnetNetwork | MstpTrunk1 | RTU3_Gym |  |  | Inputs | ChargeLossPrb | control:BooleanPoint | false {ok}
Point | BacnetNetwork | MstpTrunk1 | RTU3_Gym |  |  | Inputs | LoPress1Prb | control:BooleanPoint | false {ok}
Point | BacnetNetwork | MstpTrunk1 | RTU3_Gym |  |  | Inputs | LoChargePrb | control:BooleanPoint | false {ok}
Point | BacnetNetwork | MstpTrunk1 | RTU3_Gym |  |  | Inputs | HiDLTempPrb | control:BooleanPoint | false {ok}
Point | BacnetNetwork | MstpTrunk1 | RTU3_Gym |  |  | Inputs | INVCompPrb | control:BooleanPoint | false {ok}
Point | BacnetNetwork | MstpTrunk1 | RTU3_Gym |  |  | Inputs | OAFanPrb | control:BooleanPoint | false {ok}
Point | BacnetNetwork | MstpTrunk1 | RTU3_Gym |  |  | Inputs | LoPressDiffPrb | control:BooleanPoint | false {ok}
Point | BacnetNetwork | MstpTrunk1 | RTU3_Gym |  |  | Inputs | ExhFanState | control:BooleanPoint | false {ok}
Point | BacnetNetwork | MstpTrunk1 | RTU3_Gym |  |  | Inputs | DirtyFilterSw | control:BooleanPoint | ""true {alarm | unackedAlarm}""
Point | BacnetNetwork | MstpTrunk1 | RTU3_Gym |  |  | Inputs | HiPress1Sw | control:BooleanPoint | true {ok}
Point | BacnetNetwork | MstpTrunk1 | RTU3_Gym |  |  | Inputs | AirFlwSw | control:BooleanPoint | true {ok}
Point | BacnetNetwork | MstpTrunk1 | RTU3_Gym |  |  | Inputs | Ret.ExhFanWrn | control:BooleanPoint | false {ok}
Point | BacnetNetwork | MstpTrunk1 | RTU3_Gym |  |  | Inputs | DuctHiLmtSw | control:BooleanPoint | true {ok}
Point | BacnetNetwork | MstpTrunk1 | RTU3_Gym |  |  | Inputs | EmergencyOffSw | control:BooleanPoint | true {ok}
Point | BacnetNetwork | MstpTrunk1 | RTU3_Gym |  |  | Inputs | ReheatCapacity | control:NumericPoint | 0.00 {ok}
Point | BacnetNetwork | MstpTrunk1 | RTU3_Gym |  |  | Inputs | OAFlow | control:NumericPoint | 636.01 {ok}
Point | BacnetNetwork | MstpTrunk1 | RTU3_Gym |  |  | SetPoints | UnoccCoolSetpt | control:NumericWritable | 85.00 {ok} @ 10
Point | BacnetNetwork | MstpTrunk1 | RTU3_Gym |  |  | SetPoints | UnoccHeatSetpt | control:NumericWritable | 65.00 {ok} @ 10
Point | BacnetNetwork | MstpTrunk1 | RTU3_Gym |  |  | SetPoints | OccCoolSP | control:NumericWritable | 72.00 {overridden} @ 8
Point | BacnetNetwork | MstpTrunk1 | RTU3_Gym |  |  | SetPoints | OccHeatSP | control:NumericWritable | 68.00 {ok} @ 10
Point | BacnetNetwork | MstpTrunk1 | RTU3_Gym |  |  | SetPoints | DAClgSetpt | control:NumericWritable | 55.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk1 | RTU3_Gym |  |  | SetPoints | DefaultDATClgSetpt | control:NumericWritable | 55.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk1 | RTU3_Gym |  |  | SetPoints | DefaultDATHtgSetpt | control:NumericWritable | 120.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk1 | RTU3_Gym |  |  | SetPoints | DAHtgSetpt | control:NumericWritable | 100.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk1 | RTU3_Gym |  |  | SetPoints | HumiditySP | control:NumericWritable | 50.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk1 | RTU3_Gym |  |  | SetPoints | EmergOverride | control:EnumWritable | Normal {ok} @ def
Point | BacnetNetwork | MstpTrunk1 | RTU3_Gym |  |  | SetPoints | BldgStaticSP | control:NumericWritable | 0.05 {ok} @ def
Point | BacnetNetwork | MstpTrunk1 | RTU3_Gym |  |  | SetPoints | DACMWUSpt | control:NumericWritable | 65.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk1 | RTU3_Gym |  |  | SetPoints | ExhRetFanCtrl | control:EnumWritable | BldgP(2) {ok} @ def
Point | BacnetNetwork | MstpTrunk1 | RTU3_Gym |  |  | SetPoints | MinDehumLCTSpt | control:NumericWritable | 52.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk1 | RTU3_Gym |  |  | SetPoints | EffDATempSP | control:NumericPoint | 55.00 {ok}
Point | BacnetNetwork | MstpTrunk1 | RTU3_Gym |  |  | SetPoints | DewpointSP | control:NumericWritable | 50.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk1 | RTU3_Gym |  |  | SetPoints | CtrlTempScr | control:EnumWritable | Space {ok} @ def
Point | BacnetNetwork | MstpTrunk1 | RTU3_Gym |  |  | SetPoints | SupFanCtrl | control:EnumWritable | 1ZnVAV {ok} @ def
Point | BacnetNetwork | MstpTrunk1 | RTU3_Gym |  |  | SetPoints | DemandShed | control:EnumWritable | Auto {ok} @ def
Point | BacnetNetwork | MstpTrunk1 | RTU3_Gym |  |  | Monitor | ActiveFault | control:NumericPoint | 0.00 {ok}
Point | BacnetNetwork | MstpTrunk1 | RTU3_Gym |  |  | Monitor | ActiveProblem | control:NumericPoint | 0.00 {ok}
Point | BacnetNetwork | MstpTrunk1 | RTU3_Gym |  |  | Monitor | ActiveWarning | control:NumericPoint | 0.00 {ok}
Point | BacnetNetwork | MstpTrunk1 | RTU3_Gym |  |  | Monitor | AlarmValue | control:NumericPoint | 0.00 {ok}
Point | BacnetNetwork | MstpTrunk1 | RTU3_Gym |  |  | Monitor | UnitState | control:EnumPoint | FanOnly {ok}
Point | BacnetNetwork | MstpTrunk1 | RTU3_Gym |  |  | Monitor | MWUStatus | control:EnumPoint | Inactive {ok}
Point | BacnetNetwork | MstpTrunk1 | RTU3_Gym |  |  | Monitor | ClgStatus | control:EnumPoint | Enabled {ok}
Point | BacnetNetwork | MstpTrunk1 | RTU3_Gym |  |  | Monitor | EconoStatus | control:EnumPoint | Enabled {ok}
Point | BacnetNetwork | MstpTrunk1 | RTU3_Gym |  |  | Monitor | HtgStatus | control:EnumPoint | Enabled {ok}
Point | BacnetNetwork | MstpTrunk1 | RTU3_Gym |  |  | Monitor | EffectOccup | control:EnumPoint | Occ {ok}
Point | BacnetNetwork | MstpTrunk1 | RTU3_Gym |  |  | Monitor | McQuayStatus | control:EnumPoint | Enabled {ok}
Point | BacnetNetwork | MstpTrunk1 | RTU3_Gym |  |  | Monitor | ERWhlOnOff | control:EnumWritable | Off {ok} @ def
Point | BacnetNetwork | MstpTrunk1 | RTU3_Gym |  |  | Monitor | ClearAlarms | control:EnumWritable | No {ok} @ def
Point | BacnetNetwork | MstpTrunk1 | RTU3_Gym |  |  | Monitor | DehumStatus | control:EnumPoint | Disable {ok}
Point | BacnetNetwork | MstpTrunk1 | RTU3_Gym |  |  | Monitor | UseTstatSpts | control:EnumWritable | No {ok} @ def
Point | BacnetNetwork | MstpTrunk1 | RTU3_Gym |  |  | Monitor | ApplicCmd | control:EnumWritable | Auto {ok} @ def
Point | BacnetNetwork | MstpTrunk1 | RTU3_Gym |  |  | Schedule | OccManCmd | control:EnumWritable | Occ {ok} @ 16
Point | BacnetNetwork | MstpTrunk1 | RTU3_Gym |  |  | Schedule | SetReset | kitControl:BqlExprComponent | false | {ok}
Point | BacnetNetwork | MstpTrunk1 | RTU3_Gym |  |  | Schedule | RTU3_OptStartStop | vykonPro:OptStartStop | N/A

## UV_RM101
Type | Network | Trunk | Device | Address | DeviceType | PointFolder | PointName | PointType | Value | Status
Point | BacnetNetwork | MstpTrunk2 | UV_RM101 |  |  | Inputs | DaTemp | control:NumericPoint | 55.82 {unackedAlarm}
Point | BacnetNetwork | MstpTrunk2 | UV_RM101 |  |  | Inputs | SpaceTemp | control:NumericPoint | ""65.15 {alarm | unackedAlarm}""
Point | BacnetNetwork | MstpTrunk2 | UV_RM101 |  |  | Inputs | SpaceHumidity | control:NumericPoint | 53.30 {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_RM101 |  |  | Inputs | SpaceCO2 | control:NumericPoint | 410.00 {unackedAlarm}
Point | BacnetNetwork | MstpTrunk2 | UV_RM101 |  |  | Inputs | SupplyFanSts | control:BooleanPoint | true {unackedAlarm}
Point | BacnetNetwork | MstpTrunk2 | UV_RM101 |  |  | Inputs | CFSAlm | control:BooleanPoint | false {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_RM101 |  |  | Inputs | GpsSts | control:BooleanPoint | true {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_RM101 |  |  | Inputs | HighAlmSp | kitControl:NumericSwitch | 85.00 {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_RM101 |  |  | Inputs | Add | kitControl:Add | 88.00 {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_RM101 |  |  | Inputs | Subtract | kitControl:Subtract | 62.00 {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_RM101 |  |  | Inputs | SpaceTempAlmEnabOfst | control:NumericWritable | 3.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM101 |  |  | Inputs | SpaceTempAlmDsblDb | control:NumericWritable | 2.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM101 |  |  | Inputs | LowAlmSp | kitControl:NumericSwitch | 65.00 {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_RM101 |  |  | Inputs | Not | kitControl:Not | false {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_RM101 |  |  | Inputs | DaTempHiAlmSp | control:NumericWritable | 100.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM101 |  |  | Inputs | DaTempLoAlmSp | control:NumericWritable | 45.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM101 |  |  | Inputs | DaTempAlmDsblDb | control:NumericWritable | 3.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM101 |  |  | Inputs | DxCallForFan | control:BooleanPoint | true {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_RM101 |  |  | Outputs | SFLowSpdCmd | control:BooleanPoint | true {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_RM101 |  |  | Outputs | SFMedSpdCmd | control:BooleanPoint | false {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_RM101 |  |  | Outputs | SFHiSpdCmd | control:BooleanPoint | false {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_RM101 |  |  | Outputs | VRVEnable | control:BooleanWritable | false {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM101 |  |  | Outputs | SteamVlvSig | control:NumericWritable | 0.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM101 |  |  | Outputs | OaDmprCtrl | control:NumericWritable | 0.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM101 |  |  | Outputs | Or | kitControl:Or | true {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_RM101 |  |  | Overrides | Ov_SpaceTemp | control:NumericWritable | +inf {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM101 |  |  | Overrides | Ov_FanCmd | control:EnumWritable | Auto {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM101 |  |  | Setpoints | DaTempSP | control:NumericWritable | 100.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM101 |  |  | Setpoints | MinDaTempSP | control:NumericWritable | 60.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM101 |  |  | Setpoints | CO2LowLvlSP | control:NumericWritable | 400.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM101 |  |  | Setpoints | CO2HiLvlSP | control:NumericWritable | 1000.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM101 |  |  | Setpoints | OccClgSP | control:NumericWritable | 74.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM101 |  |  | Setpoints | UnoccClgSP | control:NumericWritable | 85.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM101 |  |  | Setpoints | OccHtgSP | control:NumericWritable | 70.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM101 |  |  | Setpoints | UnoccHtgSP | control:NumericWritable | 65.00 {overridden} @ 8
Point | BacnetNetwork | MstpTrunk2 | UV_RM101 |  |  | Setpoints | OaClgEnableSP | control:NumericWritable | 55.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM101 |  |  | Setpoints | OaHtgEnableSP | control:NumericWritable | 60.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM101 |  |  | Setpoints | SpaceTempSP | control:NumericWritable | 71.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM101 |  |  | Setpoints | EconMinPosSP | control:NumericWritable | 0.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM101 |  |  | Setpoints | NormalOprFanSpdSp | control:EnumWritable | LoSpd {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM101 |  |  | Setpoints | VRVOprFanSpdSp | control:EnumWritable | HiSpd {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM101 |  |  | Setpoints | FrzstatLatchReset_OS | kitControl:OneShot | false {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_RM101 |  |  | Setpoints | FilterRuntimeRst | control:BooleanWritable | false {ok} @ 10
Point | BacnetNetwork | MstpTrunk2 | UV_RM101 |  |  | Setpoints | FilterRuntimeReset_OS | kitControl:OneShot | false {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_RM101 |  |  | Setpoints | AllowEconOpr | control:BooleanWritable | false {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM101 |  |  | Setpoints | Heating_PID_tr | control:NumericWritable | 10.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM101 |  |  | Setpoints | Heating_PID_maxAo | control:NumericWritable | 0.10 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM101 |  |  | Setpoints | Heating_PID_minAo | control:NumericWritable | 0.10 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM101 |  |  | Setpoints | AV_RandomStartDelay | control:NumericWritable | 1.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM101 |  |  | Network | Schedule | control:BooleanWritable | false {ok} @ 16
Point | BacnetNetwork | MstpTrunk2 | UV_RM101 |  |  | Network | OaTemp | control:NumericWritable | 58.91 {ok} @ 10
Point | BacnetNetwork | MstpTrunk2 | UV_RM101 |  |  | Network | HWSEnable | control:BooleanWritable | true {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM101 |  |  | Network | OSS | control:BooleanWritable | false {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM101 |  |  | Network | SetReset | kitControl:BqlExprComponent | false | {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_RM101 |  |  | Network | OprModeShare | control:EnumPoint | Heat {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_RM101 |  |  | Network | OptStartStop | vykonPro:OptStartStop | N/A
Point | BacnetNetwork | MstpTrunk2 | UV_RM101 |  |  | Monitoring | EffOcc | control:BooleanPoint | false {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_RM101 |  |  | Monitoring | EffSysEnable | control:BooleanPoint | true {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_RM101 |  |  | Monitoring | EffSpaceSp | control:NumericPoint | 70.00 {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_RM101 |  |  | Monitoring | FilterMaintenanceAlarm | control:BooleanPoint | false {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_RM101 |  |  | Monitoring | EffHeatSP | control:NumericPoint | 65.00 {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_RM101 |  |  | Monitoring | EffCoolSP | control:NumericPoint | 85.00 {ok}

## UV_RM102
Type | Network | Trunk | Device | Address | DeviceType | PointFolder | PointName | PointType | Value | Status
Point | BacnetNetwork | MstpTrunk2 | UV_RM102 |  |  | Inputs | DaTemp | control:NumericPoint | 51.26 {unackedAlarm}
Point | BacnetNetwork | MstpTrunk2 | UV_RM102 |  |  | Inputs | SpaceTemp | control:NumericPoint | ""64.72 {alarm | unackedAlarm}""
Point | BacnetNetwork | MstpTrunk2 | UV_RM102 |  |  | Inputs | SpaceHumidity | control:NumericPoint | 52.46 {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_RM102 |  |  | Inputs | SpaceCO2 | control:NumericPoint | 407.00 {unackedAlarm}
Point | BacnetNetwork | MstpTrunk2 | UV_RM102 |  |  | Inputs | SupplyFanSts | control:BooleanPoint | true {unackedAlarm}
Point | BacnetNetwork | MstpTrunk2 | UV_RM102 |  |  | Inputs | CFSAlm | control:BooleanPoint | false {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_RM102 |  |  | Inputs | GpsSts | control:BooleanPoint | true {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_RM102 |  |  | Inputs | HighAlmSp | kitControl:NumericSwitch | 85.00 {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_RM102 |  |  | Inputs | Add | kitControl:Add | 88.00 {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_RM102 |  |  | Inputs | Subtract | kitControl:Subtract | 62.00 {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_RM102 |  |  | Inputs | SpaceTempAlmEnabOfst | control:NumericWritable | 3.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM102 |  |  | Inputs | SpaceTempAlmDsblDb | control:NumericWritable | 2.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM102 |  |  | Inputs | LowAlmSp | kitControl:NumericSwitch | 65.00 {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_RM102 |  |  | Inputs | Not | kitControl:Not | false {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_RM102 |  |  | Inputs | DaTempHiAlmSp | control:NumericWritable | 100.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM102 |  |  | Inputs | DaTempLoAlmSp | control:NumericWritable | 45.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM102 |  |  | Inputs | DaTempAlmDsblDb | control:NumericWritable | 3.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM102 |  |  | Inputs | DxCallForFan | control:BooleanPoint | false {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_RM102 |  |  | Outputs | SFLowSpdCmd | control:BooleanPoint | true {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_RM102 |  |  | Outputs | SFMedSpdCmd | control:BooleanPoint | false {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_RM102 |  |  | Outputs | SFHiSpdCmd | control:BooleanPoint | false {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_RM102 |  |  | Outputs | VRVEnable | control:BooleanWritable | false {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM102 |  |  | Outputs | SteamVlvSig | control:NumericWritable | 0.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM102 |  |  | Outputs | OaDmprCtrl | control:NumericWritable | 0.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM102 |  |  | Outputs | Or | kitControl:Or | true {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_RM102 |  |  | Overrides | Ov_SpaceTemp | control:NumericWritable | +inf {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM102 |  |  | Overrides | Ov_FanCmd | control:EnumWritable | Auto {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM102 |  |  | Setpoints | DaTempSP | control:NumericWritable | 100.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM102 |  |  | Setpoints | MinDaTempSP | control:NumericWritable | 60.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM102 |  |  | Setpoints | CO2LowLvlSP | control:NumericWritable | 400.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM102 |  |  | Setpoints | CO2HiLvlSP | control:NumericWritable | 1000.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM102 |  |  | Setpoints | OccClgSP | control:NumericWritable | 74.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM102 |  |  | Setpoints | UnoccClgSP | control:NumericWritable | 85.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM102 |  |  | Setpoints | OccHtgSP | control:NumericWritable | 70.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM102 |  |  | Setpoints | UnoccHtgSP | control:NumericWritable | 65.00 {overridden} @ 8
Point | BacnetNetwork | MstpTrunk2 | UV_RM102 |  |  | Setpoints | OaClgEnableSP | control:NumericWritable | 55.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM102 |  |  | Setpoints | OaHtgEnableSP | control:NumericWritable | 60.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM102 |  |  | Setpoints | SpaceTempSP | control:NumericWritable | 72.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM102 |  |  | Setpoints | EconMinPosSP | control:NumericWritable | 0.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM102 |  |  | Setpoints | NormalOprFanSpdSp | control:EnumWritable | LoSpd {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM102 |  |  | Setpoints | VRVOprFanSpdSp | control:EnumWritable | HiSpd {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM102 |  |  | Setpoints | FrzstatLatchReset_OS | kitControl:OneShot | false {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_RM102 |  |  | Setpoints | FilterRuntimeRst | control:BooleanWritable | false {ok} @ 10
Point | BacnetNetwork | MstpTrunk2 | UV_RM102 |  |  | Setpoints | FilterRuntimeReset_OS | kitControl:OneShot | false {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_RM102 |  |  | Setpoints | AllowEconOpr | control:BooleanWritable | false {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM102 |  |  | Setpoints | Heating_PID_tr | control:NumericWritable | 10.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM102 |  |  | Setpoints | Heating_PID_maxAo | control:NumericWritable | 0.10 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM102 |  |  | Setpoints | Heating_PID_minAo | control:NumericWritable | 0.10 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM102 |  |  | Network | Schedule | control:BooleanWritable | false {ok} @ 16
Point | BacnetNetwork | MstpTrunk2 | UV_RM102 |  |  | Network | OaTemp | control:NumericWritable | 58.91 {ok} @ 10
Point | BacnetNetwork | MstpTrunk2 | UV_RM102 |  |  | Network | HWSEnable | control:BooleanWritable | true {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM102 |  |  | Network | TextBlock | baja:WsTextBlock | N/A
Point | BacnetNetwork | MstpTrunk2 | UV_RM102 |  |  | Network | OSS | control:BooleanWritable | false {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM102 |  |  | Network | SetReset | kitControl:BqlExprComponent | false | {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_RM102 |  |  | Network | OprModeShare | control:EnumPoint | Heat {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_RM102 |  |  | Network | OptStartStop | vykonPro:OptStartStop | N/A
Point | BacnetNetwork | MstpTrunk2 | UV_RM102 |  |  | Monitoring | EffOcc | control:BooleanPoint | false {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_RM102 |  |  | Monitoring | EffSysEnable | control:BooleanPoint | true {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_RM102 |  |  | Monitoring | EffSpaceSp | control:NumericPoint | 70.00 {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_RM102 |  |  | Monitoring | FilterMaintenanceAlarm | control:BooleanPoint | false {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_RM102 |  |  | Monitoring | EffHeatSP | control:NumericPoint | 65.00 {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_RM102 |  |  | Monitoring | EffCoolSP | control:NumericPoint | 85.00 {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_RM102 |  |  | AV_RandomStartDelay | Proxy Ext | bacnet:BacnetNumericProxyExt | 1.00 | {ok}

## UV_RM103
Type | Network | Trunk | Device | Address | DeviceType | PointFolder | PointName | PointType | Value | Status
Point | BacnetNetwork | MstpTrunk2 | UV_RM103 |  |  | Inputs | DaTemp | control:NumericPoint | 73.51 {unackedAlarm} alarmInhibit
Point | BacnetNetwork | MstpTrunk2 | UV_RM103 |  |  | Inputs | SpaceTemp | control:NumericPoint | 69.38 {unackedAlarm}
Point | BacnetNetwork | MstpTrunk2 | UV_RM103 |  |  | Inputs | SpaceHumidity | control:NumericPoint | 45.46 {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_RM103 |  |  | Inputs | SpaceCO2 | control:NumericPoint | 406.00 {unackedAlarm}
Point | BacnetNetwork | MstpTrunk2 | UV_RM103 |  |  | Inputs | SupplyFanSts | control:BooleanPoint | false {unackedAlarm}
Point | BacnetNetwork | MstpTrunk2 | UV_RM103 |  |  | Inputs | CFSAlm | control:BooleanPoint | false {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_RM103 |  |  | Inputs | GpsSts | control:BooleanPoint | true {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_RM103 |  |  | Inputs | HighAlmSp | kitControl:NumericSwitch | 85.00 {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_RM103 |  |  | Inputs | Add | kitControl:Add | 88.00 {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_RM103 |  |  | Inputs | Subtract | kitControl:Subtract | 62.00 {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_RM103 |  |  | Inputs | SpaceTempAlmEnabOfst | control:NumericWritable | 3.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM103 |  |  | Inputs | SpaceTempAlmDsblDb | control:NumericWritable | 2.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM103 |  |  | Inputs | LowAlmSp | kitControl:NumericSwitch | 65.00 {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_RM103 |  |  | Inputs | Not | kitControl:Not | true {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_RM103 |  |  | Inputs | DaTempHiAlmSp | control:NumericWritable | 100.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM103 |  |  | Inputs | DaTempLoAlmSp | control:NumericWritable | 45.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM103 |  |  | Inputs | DaTempAlmDsblDb | control:NumericWritable | 3.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM103 |  |  | Inputs | DxCallForFan | control:BooleanPoint | false {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_RM103 |  |  | Outputs | SFLowSpdCmd | control:BooleanPoint | false {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_RM103 |  |  | Outputs | SFMedSpdCmd | control:BooleanPoint | false {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_RM103 |  |  | Outputs | SFHiSpdCmd | control:BooleanPoint | false {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_RM103 |  |  | Outputs | VRVEnable | control:BooleanWritable | false {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM103 |  |  | Outputs | SteamVlvSig | control:NumericWritable | 0.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM103 |  |  | Outputs | OaDmprCtrl | control:NumericWritable | 0.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM103 |  |  | Outputs | Or | kitControl:Or | false {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_RM103 |  |  | Overrides | Ov_SpaceTemp | control:NumericWritable | +inf {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM103 |  |  | Overrides | Ov_FanCmd | control:EnumWritable | Auto {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM103 |  |  | Setpoints | DaTempSP | control:NumericWritable | 100.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM103 |  |  | Setpoints | MinDaTempSP | control:NumericWritable | 60.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM103 |  |  | Setpoints | CO2LowLvlSP | control:NumericWritable | 400.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM103 |  |  | Setpoints | CO2HiLvlSP | control:NumericWritable | 1000.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM103 |  |  | Setpoints | OccClgSP | control:NumericWritable | 74.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM103 |  |  | Setpoints | UnoccClgSP | control:NumericWritable | 85.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM103 |  |  | Setpoints | OccHtgSP | control:NumericWritable | 70.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM103 |  |  | Setpoints | UnoccHtgSP | control:NumericWritable | 65.00 {overridden} @ 8
Point | BacnetNetwork | MstpTrunk2 | UV_RM103 |  |  | Setpoints | OaClgEnableSP | control:NumericWritable | 55.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM103 |  |  | Setpoints | OaHtgEnableSP | control:NumericWritable | 60.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM103 |  |  | Setpoints | SpaceTempSP | control:NumericWritable | 69.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM103 |  |  | Setpoints | EconMinPosSP | control:NumericWritable | 0.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM103 |  |  | Setpoints | NormalOprFanSpdSp | control:EnumWritable | LoSpd {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM103 |  |  | Setpoints | VRVOprFanSpdSp | control:EnumWritable | HiSpd {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM103 |  |  | Setpoints | FrzstatLatchReset_OS | kitControl:OneShot | false {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_RM103 |  |  | Setpoints | FilterRuntimeRst | control:BooleanWritable | false {ok} @ 10
Point | BacnetNetwork | MstpTrunk2 | UV_RM103 |  |  | Setpoints | FilterRuntimeReset_OS | kitControl:OneShot | false {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_RM103 |  |  | Setpoints | AllowEconOpr | control:BooleanWritable | false {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM103 |  |  | Setpoints | Heating_PID_minAo | control:NumericWritable | 0.10 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM103 |  |  | Setpoints | Heating_PID_maxAo | control:NumericWritable | 0.10 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM103 |  |  | Setpoints | Heating_PID_tr | control:NumericWritable | 10.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM103 |  |  | Network | Schedule | control:BooleanWritable | false {ok} @ 16
Point | BacnetNetwork | MstpTrunk2 | UV_RM103 |  |  | Network | OaTemp | control:NumericWritable | 58.91 {ok} @ 10
Point | BacnetNetwork | MstpTrunk2 | UV_RM103 |  |  | Network | HWSEnable | control:BooleanWritable | true {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM103 |  |  | Network | TextBlock | baja:WsTextBlock | N/A
Point | BacnetNetwork | MstpTrunk2 | UV_RM103 |  |  | Network | OSS | control:BooleanWritable | false {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM103 |  |  | Network | SetReset | kitControl:BqlExprComponent | false | {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_RM103 |  |  | Network | OprModeShare | control:EnumPoint | Fan {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_RM103 |  |  | Network | OptStartStop | vykonPro:OptStartStop | N/A
Point | BacnetNetwork | MstpTrunk2 | UV_RM103 |  |  | Monitoring | EffOcc | control:BooleanPoint | false {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_RM103 |  |  | Monitoring | EffSysEnable | control:BooleanPoint | false {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_RM103 |  |  | Monitoring | EffSpaceSp | control:NumericPoint | 70.00 {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_RM103 |  |  | Monitoring | FilterMaintenanceAlarm | control:BooleanPoint | false {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_RM103 |  |  | Monitoring | EffHeatSP | control:NumericPoint | 65.00 {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_RM103 |  |  | Monitoring | EffCoolSP | control:NumericPoint | 85.00 {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_RM103 |  |  | AV_RandomStartDelay | Proxy Ext | bacnet:BacnetNumericProxyExt | 1.00 | {ok}

## UV_RM104
Type | Network | Trunk | Device | Address | DeviceType | PointFolder | PointName | PointType | Value | Status
Point | BacnetNetwork | MstpTrunk2 | UV_RM104 |  |  | Inputs | DaTemp | control:NumericPoint | 52.02 {unackedAlarm}
Point | BacnetNetwork | MstpTrunk2 | UV_RM104 |  |  | Inputs | SpaceTemp | control:NumericPoint | ""63.77 {alarm | unackedAlarm}""
Point | BacnetNetwork | MstpTrunk2 | UV_RM104 |  |  | Inputs | SpaceHumidity | control:NumericPoint | 56.71 {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_RM104 |  |  | Inputs | SpaceCO2 | control:NumericPoint | 407.00 {unackedAlarm}
Point | BacnetNetwork | MstpTrunk2 | UV_RM104 |  |  | Inputs | SupplyFanSts | control:BooleanPoint | true {unackedAlarm}
Point | BacnetNetwork | MstpTrunk2 | UV_RM104 |  |  | Inputs | CFSAlm | control:BooleanPoint | false {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_RM104 |  |  | Inputs | GpsSts | control:BooleanPoint | false {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_RM104 |  |  | Inputs | HighAlmSp | kitControl:NumericSwitch | 75.00 {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_RM104 |  |  | Inputs | Add | kitControl:Add | 78.00 {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_RM104 |  |  | Inputs | Subtract | kitControl:Subtract | 62.00 {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_RM104 |  |  | Inputs | SpaceTempAlmEnabOfst | control:NumericWritable | 3.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM104 |  |  | Inputs | SpaceTempAlmDsblDb | control:NumericWritable | 2.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM104 |  |  | Inputs | LowAlmSp | kitControl:NumericSwitch | 65.00 {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_RM104 |  |  | Inputs | Not | kitControl:Not | false {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_RM104 |  |  | Inputs | DaTempHiAlmSp | control:NumericWritable | 100.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM104 |  |  | Inputs | DaTempLoAlmSp | control:NumericWritable | 45.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM104 |  |  | Inputs | DaTempAlmDsblDb | control:NumericWritable | 3.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM104 |  |  | Inputs | DxCallForFan | control:BooleanPoint | true {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_RM104 |  |  | Outputs | SFLowSpdCmd | control:BooleanPoint | true {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_RM104 |  |  | Outputs | SFMedSpdCmd | control:BooleanPoint | false {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_RM104 |  |  | Outputs | SFHiSpdCmd | control:BooleanPoint | false {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_RM104 |  |  | Outputs | VRVEnable | control:BooleanWritable | false {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM104 |  |  | Outputs | SteamVlvSig | control:NumericWritable | 0.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM104 |  |  | Outputs | OaDmprCtrl | control:NumericWritable | 0.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM104 |  |  | Outputs | Or | kitControl:Or | true {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_RM104 |  |  | Overrides | Ov_SpaceTemp | control:NumericWritable | +inf {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM104 |  |  | Overrides | Ov_FanCmd | control:EnumWritable | Auto {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM104 |  |  | Setpoints | DaTempSP | control:NumericWritable | 100.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM104 |  |  | Setpoints | MinDaTempSP | control:NumericWritable | 60.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM104 |  |  | Setpoints | CO2LowLvlSP | control:NumericWritable | 400.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM104 |  |  | Setpoints | CO2HiLvlSP | control:NumericWritable | 1000.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM104 |  |  | Setpoints | OccClgSP | control:NumericWritable | 74.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM104 |  |  | Setpoints | UnoccClgSP | control:NumericWritable | 75.00 {overridden} @ 8
Point | BacnetNetwork | MstpTrunk2 | UV_RM104 |  |  | Setpoints | OccHtgSP | control:NumericWritable | 70.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM104 |  |  | Setpoints | UnoccHtgSP | control:NumericWritable | 65.00 {overridden} @ 8
Point | BacnetNetwork | MstpTrunk2 | UV_RM104 |  |  | Setpoints | OaClgEnableSP | control:NumericWritable | 55.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM104 |  |  | Setpoints | OaHtgEnableSP | control:NumericWritable | 60.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM104 |  |  | Setpoints | SpaceTempSP | control:NumericWritable | 69.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM104 |  |  | Setpoints | EconMinPosSP | control:NumericWritable | 0.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM104 |  |  | Setpoints | NormalOprFanSpdSp | control:EnumWritable | LoSpd {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM104 |  |  | Setpoints | VRVOprFanSpdSp | control:EnumWritable | HiSpd {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM104 |  |  | Setpoints | FrzstatLatchReset_OS | kitControl:OneShot | false {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_RM104 |  |  | Setpoints | FilterRuntimeRst | control:BooleanWritable | false {ok} @ 10
Point | BacnetNetwork | MstpTrunk2 | UV_RM104 |  |  | Setpoints | FilterRuntimeReset_OS | kitControl:OneShot | false {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_RM104 |  |  | Setpoints | AllowEconOpr | control:BooleanWritable | false {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM104 |  |  | Setpoints | Heating_PID_minAo | control:NumericWritable | 0.10 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM104 |  |  | Setpoints | Heating_PID_maxAo | control:NumericWritable | 0.10 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM104 |  |  | Setpoints | Heating_PID_tr | control:NumericWritable | 10.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM104 |  |  | Network | Schedule | control:BooleanWritable | false {ok} @ 16
Point | BacnetNetwork | MstpTrunk2 | UV_RM104 |  |  | Network | OaTemp | control:NumericWritable | 58.91 {ok} @ 10
Point | BacnetNetwork | MstpTrunk2 | UV_RM104 |  |  | Network | HWSEnable | control:BooleanWritable | true {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM104 |  |  | Network | TextBlock | baja:WsTextBlock | N/A
Point | BacnetNetwork | MstpTrunk2 | UV_RM104 |  |  | Network | OSS | control:BooleanWritable | false {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM104 |  |  | Network | SetReset | kitControl:BqlExprComponent | false | {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_RM104 |  |  | Network | OprModeShare | control:EnumPoint | Heat {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_RM104 |  |  | Network | OptStartStop | vykonPro:OptStartStop | N/A
Point | BacnetNetwork | MstpTrunk2 | UV_RM104 |  |  | Monitoring | EffOcc | control:BooleanPoint | false {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_RM104 |  |  | Monitoring | EffSysEnable | control:BooleanPoint | true {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_RM104 |  |  | Monitoring | EffSpaceSp | control:NumericPoint | 70.00 {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_RM104 |  |  | Monitoring | FilterMaintenanceAlarm | control:BooleanPoint | false {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_RM104 |  |  | Monitoring | EffHeatSP | control:NumericPoint | 65.00 {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_RM104 |  |  | Monitoring | EffCoolSP | control:NumericPoint | 75.00 {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_RM104 |  |  | AV_RandomStartDelay | Proxy Ext | bacnet:BacnetNumericProxyExt | 1.00 | {ok}

## UV_RM105
Type | Network | Trunk | Device | Address | DeviceType | PointFolder | PointName | PointType | Value | Status
Point | BacnetNetwork | MstpTrunk2 | UV_RM105 |  |  | Inputs | DaTemp | control:NumericPoint | 77.10 {unackedAlarm} alarmInhibit
Point | BacnetNetwork | MstpTrunk2 | UV_RM105 |  |  | Inputs | SpaceTemp | control:NumericPoint | 71.88 {unackedAlarm}
Point | BacnetNetwork | MstpTrunk2 | UV_RM105 |  |  | Inputs | SpaceHumidity | control:NumericPoint | 36.92 {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_RM105 |  |  | Inputs | SpaceCO2 | control:NumericPoint | 406.00 {unackedAlarm}
Point | BacnetNetwork | MstpTrunk2 | UV_RM105 |  |  | Inputs | SupplyFanSts | control:BooleanPoint | false {unackedAlarm}
Point | BacnetNetwork | MstpTrunk2 | UV_RM105 |  |  | Inputs | CFSAlm | control:BooleanPoint | false {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_RM105 |  |  | Inputs | GpsSts | control:BooleanPoint | true {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_RM105 |  |  | Inputs | HighAlmSp | kitControl:NumericSwitch | 85.00 {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_RM105 |  |  | Inputs | Add | kitControl:Add | 88.00 {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_RM105 |  |  | Inputs | Subtract | kitControl:Subtract | 62.00 {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_RM105 |  |  | Inputs | SpaceTempAlmEnabOfst | control:NumericWritable | 3.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM105 |  |  | Inputs | SpaceTempAlmDsblDb | control:NumericWritable | 2.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM105 |  |  | Inputs | LowAlmSp | kitControl:NumericSwitch | 65.00 {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_RM105 |  |  | Inputs | Not | kitControl:Not | true {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_RM105 |  |  | Inputs | DaTempHiAlmSp | control:NumericWritable | 100.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM105 |  |  | Inputs | DaTempLoAlmSp | control:NumericWritable | 45.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM105 |  |  | Inputs | DaTempAlmDsblDb | control:NumericWritable | 3.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM105 |  |  | Inputs | DxCallForFan | control:BooleanPoint | false {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_RM105 |  |  | Outputs | SFLowSpdCmd | control:BooleanPoint | false {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_RM105 |  |  | Outputs | SFMedSpdCmd | control:BooleanPoint | false {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_RM105 |  |  | Outputs | SFHiSpdCmd | control:BooleanPoint | false {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_RM105 |  |  | Outputs | VRVEnable | control:BooleanWritable | false {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM105 |  |  | Outputs | SteamVlvSig | control:NumericWritable | 0.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM105 |  |  | Outputs | OaDmprCtrl | control:NumericWritable | 0.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM105 |  |  | Outputs | Or | kitControl:Or | false {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_RM105 |  |  | Overrides | Ov_SpaceTemp | control:NumericWritable | +inf {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM105 |  |  | Overrides | Ov_FanCmd | control:EnumWritable | Auto {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM105 |  |  | Setpoints | DaTempSP | control:NumericWritable | 100.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM105 |  |  | Setpoints | MinDaTempSP | control:NumericWritable | 60.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM105 |  |  | Setpoints | CO2LowLvlSP | control:NumericWritable | 400.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM105 |  |  | Setpoints | CO2HiLvlSP | control:NumericWritable | 1000.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM105 |  |  | Setpoints | OccClgSP | control:NumericWritable | 74.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM105 |  |  | Setpoints | UnoccClgSP | control:NumericWritable | 85.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM105 |  |  | Setpoints | OccHtgSP | control:NumericWritable | 70.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM105 |  |  | Setpoints | UnoccHtgSP | control:NumericWritable | 65.00 {overridden} @ 8
Point | BacnetNetwork | MstpTrunk2 | UV_RM105 |  |  | Setpoints | OaClgEnableSP | control:NumericWritable | 55.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM105 |  |  | Setpoints | OaHtgEnableSP | control:NumericWritable | 60.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM105 |  |  | Setpoints | SpaceTempSP | control:NumericWritable | 72.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM105 |  |  | Setpoints | EconMinPosSP | control:NumericWritable | 0.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM105 |  |  | Setpoints | NormalOprFanSpdSp | control:EnumWritable | LoSpd {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM105 |  |  | Setpoints | VRVOprFanSpdSp | control:EnumWritable | HiSpd {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM105 |  |  | Setpoints | FrzstatLatchReset_OS | kitControl:OneShot | false {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_RM105 |  |  | Setpoints | FilterRuntimeRst | control:BooleanWritable | false {ok} @ 10
Point | BacnetNetwork | MstpTrunk2 | UV_RM105 |  |  | Setpoints | FilterRuntimeReset_OS | kitControl:OneShot | false {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_RM105 |  |  | Setpoints | AllowEconOpr | control:BooleanWritable | false {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM105 |  |  | Setpoints | Heating_PID_minAo | control:NumericWritable | 0.10 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM105 |  |  | Setpoints | Heating_PID_maxAo | control:NumericWritable | 0.10 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM105 |  |  | Setpoints | Heating_PID_tr | control:NumericWritable | 10.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM105 |  |  | Network | Schedule | control:BooleanWritable | false {ok} @ 16
Point | BacnetNetwork | MstpTrunk2 | UV_RM105 |  |  | Network | OaTemp | control:NumericWritable | 58.91 {ok} @ 10
Point | BacnetNetwork | MstpTrunk2 | UV_RM105 |  |  | Network | HWSEnable | control:BooleanWritable | true {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM105 |  |  | Network | TextBlock | baja:WsTextBlock | N/A
Point | BacnetNetwork | MstpTrunk2 | UV_RM105 |  |  | Network | OSS | control:BooleanWritable | false {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM105 |  |  | Network | SetReset | kitControl:BqlExprComponent | false | {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_RM105 |  |  | Network | OprModeShare | control:EnumPoint | Fan {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_RM105 |  |  | Network | OptStartStop | vykonPro:OptStartStop | N/A
Point | BacnetNetwork | MstpTrunk2 | UV_RM105 |  |  | Monitoring | EffOcc | control:BooleanPoint | false {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_RM105 |  |  | Monitoring | EffSysEnable | control:BooleanPoint | false {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_RM105 |  |  | Monitoring | EffSpaceSp | control:NumericPoint | 70.00 {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_RM105 |  |  | Monitoring | FilterMaintenanceAlarm | control:BooleanPoint | false {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_RM105 |  |  | Monitoring | EffHeatSP | control:NumericPoint | 65.00 {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_RM105 |  |  | Monitoring | EffCoolSP | control:NumericPoint | 85.00 {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_RM105 |  |  | AV_RandomStartDelay | Proxy Ext | bacnet:BacnetNumericProxyExt | 1.00 | {ok}

## UV_RM106
Type | Network | Trunk | Device | Address | DeviceType | PointFolder | PointName | PointType | Value | Status
Point | BacnetNetwork | MstpTrunk2 | UV_RM106 |  |  | Inputs | DaTemp | control:NumericPoint | 73.92 {unackedAlarm}
Point | BacnetNetwork | MstpTrunk2 | UV_RM106 |  |  | Inputs | SpaceTemp | control:NumericPoint | 71.54 {unackedAlarm}
Point | BacnetNetwork | MstpTrunk2 | UV_RM106 |  |  | Inputs | SpaceHumidity | control:NumericPoint | 36.01 {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_RM106 |  |  | Inputs | SpaceCO2 | control:NumericPoint | 396.00 {unackedAlarm}
Point | BacnetNetwork | MstpTrunk2 | UV_RM106 |  |  | Inputs | SupplyFanSts | control:BooleanPoint | true {unackedAlarm}
Point | BacnetNetwork | MstpTrunk2 | UV_RM106 |  |  | Inputs | CFSAlm | control:BooleanPoint | false {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_RM106 |  |  | Inputs | GpsSts | control:BooleanPoint | true {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_RM106 |  |  | Inputs | HighAlmSp | kitControl:NumericSwitch | 74.00 {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_RM106 |  |  | Inputs | Add | kitControl:Add | 74.00 {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_RM106 |  |  | Inputs | Subtract | kitControl:Subtract | 64.00 {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_RM106 |  |  | Inputs | SpaceTempAlmEnabOfst | control:NumericWritable | 3.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM106 |  |  | Inputs | SpaceTempAlmDsblDb | control:NumericWritable | 2.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM106 |  |  | Inputs | LowAlmSp | kitControl:NumericSwitch | 64.00 {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_RM106 |  |  | Inputs | Not | kitControl:Not | false {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_RM106 |  |  | Inputs | DaTempHiAlmSp | control:NumericWritable | 100.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM106 |  |  | Inputs | DaTempLoAlmSp | control:NumericWritable | 45.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM106 |  |  | Inputs | DaTempAlmDsblDb | control:NumericWritable | 3.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM106 |  |  | Inputs | DxCallForFan | control:BooleanPoint | true {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_RM106 |  |  | Outputs | SFLowSpdCmd | control:BooleanPoint | false {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_RM106 |  |  | Outputs | SFMedSpdCmd | control:BooleanPoint | false {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_RM106 |  |  | Outputs | SFHiSpdCmd | control:BooleanPoint | true {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_RM106 |  |  | Outputs | VRVEnable | control:BooleanWritable | true {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM106 |  |  | Outputs | SteamVlvSig | control:NumericWritable | 0.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM106 |  |  | Outputs | OaDmprCtrl | control:NumericWritable | 0.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM106 |  |  | Outputs | Or | kitControl:Or | true {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_RM106 |  |  | Overrides | Ov_SpaceTemp | control:NumericWritable | +inf {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM106 |  |  | Overrides | Ov_FanCmd | control:EnumWritable | Auto {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM106 |  |  | Setpoints | DaTempSP | control:NumericWritable | 100.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM106 |  |  | Setpoints | MinDaTempSP | control:NumericWritable | 60.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM106 |  |  | Setpoints | CO2LowLvlSP | control:NumericWritable | 400.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM106 |  |  | Setpoints | CO2HiLvlSP | control:NumericWritable | 1000.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM106 |  |  | Setpoints | OccClgSP | control:NumericWritable | 74.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM106 |  |  | Setpoints | UnoccClgSP | control:NumericWritable | 85.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM106 |  |  | Setpoints | OccHtgSP | control:NumericWritable | 70.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM106 |  |  | Setpoints | UnoccHtgSP | control:NumericWritable | 65.00 {overridden} @ 8
Point | BacnetNetwork | MstpTrunk2 | UV_RM106 |  |  | Setpoints | OaClgEnableSP | control:NumericWritable | 55.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM106 |  |  | Setpoints | OaHtgEnableSP | control:NumericWritable | 60.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM106 |  |  | Setpoints | SpaceTempSP | control:NumericWritable | 72.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM106 |  |  | Setpoints | EconMinPosSP | control:NumericWritable | 0.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM106 |  |  | Setpoints | NormalOprFanSpdSp | control:EnumWritable | LoSpd {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM106 |  |  | Setpoints | VRVOprFanSpdSp | control:EnumWritable | HiSpd {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM106 |  |  | Setpoints | FrzstatLatchReset_OS | kitControl:OneShot | false {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_RM106 |  |  | Setpoints | FilterRuntimeRst | control:BooleanWritable | false {ok} @ 10
Point | BacnetNetwork | MstpTrunk2 | UV_RM106 |  |  | Setpoints | FilterRuntimeReset_OS | kitControl:OneShot | false {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_RM106 |  |  | Setpoints | AllowEconOpr | control:BooleanWritable | false {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM106 |  |  | Setpoints | Heating_PID_minAo | control:NumericWritable | 0.10 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM106 |  |  | Setpoints | Heating_PID_maxAo | control:NumericWritable | 0.10 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM106 |  |  | Setpoints | Heating_PID_tr | control:NumericWritable | 10.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM106 |  |  | Network | Schedule | control:BooleanWritable | true {overridden} @ 8
Point | BacnetNetwork | MstpTrunk2 | UV_RM106 |  |  | Network | OaTemp | control:NumericWritable | 58.91 {ok} @ 10
Point | BacnetNetwork | MstpTrunk2 | UV_RM106 |  |  | Network | HWSEnable | control:BooleanWritable | true {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM106 |  |  | Network | TextBlock | baja:WsTextBlock | N/A
Point | BacnetNetwork | MstpTrunk2 | UV_RM106 |  |  | Network | OSS | control:BooleanWritable | false {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM106 |  |  | Network | SetReset | kitControl:BqlExprComponent | false | {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_RM106 |  |  | Network | OprModeShare | control:EnumPoint | Cool {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_RM106 |  |  | Network | OptStartStop | vykonPro:OptStartStop | N/A
Point | BacnetNetwork | MstpTrunk2 | UV_RM106 |  |  | Monitoring | EffOcc | control:BooleanPoint | true {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_RM106 |  |  | Monitoring | EffSysEnable | control:BooleanPoint | true {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_RM106 |  |  | Monitoring | EffSpaceSp | control:NumericPoint | 71.00 {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_RM106 |  |  | Monitoring | FilterMaintenanceAlarm | control:BooleanPoint | false {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_RM106 |  |  | Monitoring | EffHeatSP | control:NumericPoint | 67.00 {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_RM106 |  |  | Monitoring | EffCoolSP | control:NumericPoint | 71.00 {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_RM106 |  |  | AV_RandomStartDelay | Proxy Ext | bacnet:BacnetNumericProxyExt | 1.00 | {ok}

## UV_RM107
Type | Network | Trunk | Device | Address | DeviceType | PointFolder | PointName | PointType | Value | Status
Point | BacnetNetwork | MstpTrunk2 | UV_RM107 |  |  | Inputs | DaTemp | control:NumericPoint | 75.28 {unackedAlarm} alarmInhibit
Point | BacnetNetwork | MstpTrunk2 | UV_RM107 |  |  | Inputs | SpaceTemp | control:NumericPoint | 71.78 {unackedAlarm}
Point | BacnetNetwork | MstpTrunk2 | UV_RM107 |  |  | Inputs | SpaceHumidity | control:NumericPoint | 36.50 {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_RM107 |  |  | Inputs | SpaceCO2 | control:NumericPoint | 402.00 {unackedAlarm}
Point | BacnetNetwork | MstpTrunk2 | UV_RM107 |  |  | Inputs | SupplyFanSts | control:BooleanPoint | false {unackedAlarm}
Point | BacnetNetwork | MstpTrunk2 | UV_RM107 |  |  | Inputs | CFSAlm | control:BooleanPoint | false {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_RM107 |  |  | Inputs | GpsSts | control:BooleanPoint | true {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_RM107 |  |  | Inputs | HighAlmSp | kitControl:NumericSwitch | 85.00 {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_RM107 |  |  | Inputs | Add | kitControl:Add | 88.00 {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_RM107 |  |  | Inputs | Subtract | kitControl:Subtract | 62.00 {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_RM107 |  |  | Inputs | SpaceTempAlmEnabOfst | control:NumericWritable | 3.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM107 |  |  | Inputs | SpaceTempAlmDsblDb | control:NumericWritable | 2.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM107 |  |  | Inputs | LowAlmSp | kitControl:NumericSwitch | 65.00 {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_RM107 |  |  | Inputs | Not | kitControl:Not | true {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_RM107 |  |  | Inputs | DaTempHiAlmSp | control:NumericWritable | 100.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM107 |  |  | Inputs | DaTempLoAlmSp | control:NumericWritable | 45.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM107 |  |  | Inputs | DaTempAlmDsblDb | control:NumericWritable | 3.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM107 |  |  | Inputs | DxCallForFan | control:BooleanPoint | false {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_RM107 |  |  | Outputs | SFLowSpdCmd | control:BooleanPoint | false {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_RM107 |  |  | Outputs | SFMedSpdCmd | control:BooleanPoint | false {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_RM107 |  |  | Outputs | SFHiSpdCmd | control:BooleanPoint | false {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_RM107 |  |  | Outputs | VRVEnable | control:BooleanWritable | false {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM107 |  |  | Outputs | SteamVlvSig | control:NumericWritable | 0.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM107 |  |  | Outputs | OaDmprCtrl | control:NumericWritable | 0.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM107 |  |  | Outputs | Or | kitControl:Or | false {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_RM107 |  |  | Overrides | Ov_SpaceTemp | control:NumericWritable | +inf {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM107 |  |  | Overrides | Ov_FanCmd | control:EnumWritable | Auto {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM107 |  |  | Setpoints | DaTempSP | control:NumericWritable | 100.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM107 |  |  | Setpoints | MinDaTempSP | control:NumericWritable | 60.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM107 |  |  | Setpoints | CO2LowLvlSP | control:NumericWritable | 400.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM107 |  |  | Setpoints | CO2HiLvlSP | control:NumericWritable | 1000.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM107 |  |  | Setpoints | OccClgSP | control:NumericWritable | 74.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM107 |  |  | Setpoints | UnoccClgSP | control:NumericWritable | 85.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM107 |  |  | Setpoints | OccHtgSP | control:NumericWritable | 70.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM107 |  |  | Setpoints | UnoccHtgSP | control:NumericWritable | 65.00 {overridden} @ 8
Point | BacnetNetwork | MstpTrunk2 | UV_RM107 |  |  | Setpoints | OaClgEnableSP | control:NumericWritable | 55.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM107 |  |  | Setpoints | OaHtgEnableSP | control:NumericWritable | 60.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM107 |  |  | Setpoints | SpaceTempSP | control:NumericWritable | 69.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM107 |  |  | Setpoints | EconMinPosSP | control:NumericWritable | 0.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM107 |  |  | Setpoints | NormalOprFanSpdSp | control:EnumWritable | LoSpd {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM107 |  |  | Setpoints | VRVOprFanSpdSp | control:EnumWritable | HiSpd {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM107 |  |  | Setpoints | FrzstatLatchReset_OS | kitControl:OneShot | false {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_RM107 |  |  | Setpoints | FilterRuntimeRst | control:BooleanWritable | false {ok} @ 10
Point | BacnetNetwork | MstpTrunk2 | UV_RM107 |  |  | Setpoints | FilterRuntimeReset_OS | kitControl:OneShot | false {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_RM107 |  |  | Setpoints | AllowEconOpr | control:BooleanWritable | false {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM107 |  |  | Setpoints | Heating_PID_minAo | control:NumericWritable | 0.10 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM107 |  |  | Setpoints | Heating_PID_maxAo | control:NumericWritable | 0.10 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM107 |  |  | Setpoints | Heating_PID_tr | control:NumericWritable | 10.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM107 |  |  | Network | Schedule | control:BooleanWritable | false {ok} @ 16
Point | BacnetNetwork | MstpTrunk2 | UV_RM107 |  |  | Network | OaTemp | control:NumericWritable | 58.91 {ok} @ 10
Point | BacnetNetwork | MstpTrunk2 | UV_RM107 |  |  | Network | HWSEnable | control:BooleanWritable | true {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM107 |  |  | Network | TextBlock | baja:WsTextBlock | N/A
Point | BacnetNetwork | MstpTrunk2 | UV_RM107 |  |  | Network | OSS | control:BooleanWritable | false {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM107 |  |  | Network | SetReset | kitControl:BqlExprComponent | false | {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_RM107 |  |  | Network | OprModeShare | control:EnumPoint | Fan {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_RM107 |  |  | Network | OptStartStop | vykonPro:OptStartStop | N/A
Point | BacnetNetwork | MstpTrunk2 | UV_RM107 |  |  | Monitoring | EffOcc | control:BooleanPoint | false {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_RM107 |  |  | Monitoring | EffSysEnable | control:BooleanPoint | false {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_RM107 |  |  | Monitoring | EffSpaceSp | control:NumericPoint | 70.00 {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_RM107 |  |  | Monitoring | FilterMaintenanceAlarm | control:BooleanPoint | false {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_RM107 |  |  | Monitoring | EffHeatSP | control:NumericPoint | 65.00 {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_RM107 |  |  | Monitoring | EffCoolSP | control:NumericPoint | 85.00 {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_RM107 |  |  | AV_RandomStartDelay | Proxy Ext | bacnet:BacnetNumericProxyExt | 1.00 | {ok}

## UV_RM108
Type | Network | Trunk | Device | Address | DeviceType | PointFolder | PointName | PointType | Value | Status
Point | BacnetNetwork | MstpTrunk2 | UV_RM108 |  |  | Inputs | DaTemp | control:NumericPoint | 74.36 {unackedAlarm} alarmInhibit
Point | BacnetNetwork | MstpTrunk2 | UV_RM108 |  |  | Inputs | SpaceTemp | control:NumericPoint | 70.37 {unackedAlarm}
Point | BacnetNetwork | MstpTrunk2 | UV_RM108 |  |  | Inputs | SpaceHumidity | control:NumericPoint | 42.71 {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_RM108 |  |  | Inputs | SpaceCO2 | control:NumericPoint | 401.00 {unackedAlarm}
Point | BacnetNetwork | MstpTrunk2 | UV_RM108 |  |  | Inputs | SupplyFanSts | control:BooleanPoint | false {unackedAlarm}
Point | BacnetNetwork | MstpTrunk2 | UV_RM108 |  |  | Inputs | CFSAlm | control:BooleanPoint | false {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_RM108 |  |  | Inputs | GpsSts | control:BooleanPoint | true {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_RM108 |  |  | Inputs | HighAlmSp | kitControl:NumericSwitch | 85.00 {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_RM108 |  |  | Inputs | Add | kitControl:Add | 88.00 {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_RM108 |  |  | Inputs | Subtract | kitControl:Subtract | 62.00 {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_RM108 |  |  | Inputs | SpaceTempAlmEnabOfst | control:NumericWritable | 3.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM108 |  |  | Inputs | SpaceTempAlmDsblDb | control:NumericWritable | 2.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM108 |  |  | Inputs | LowAlmSp | kitControl:NumericSwitch | 65.00 {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_RM108 |  |  | Inputs | Not | kitControl:Not | true {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_RM108 |  |  | Inputs | DaTempHiAlmSp | control:NumericWritable | 100.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM108 |  |  | Inputs | DaTempLoAlmSp | control:NumericWritable | 45.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM108 |  |  | Inputs | DaTempAlmDsblDb | control:NumericWritable | 3.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM108 |  |  | Inputs | DxCallForFan | control:BooleanPoint | false {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_RM108 |  |  | Outputs | SFLowSpdCmd | control:BooleanPoint | false {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_RM108 |  |  | Outputs | SFMedSpdCmd | control:BooleanPoint | false {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_RM108 |  |  | Outputs | SFHiSpdCmd | control:BooleanPoint | false {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_RM108 |  |  | Outputs | VRVEnable | control:BooleanWritable | false {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM108 |  |  | Outputs | SteamVlvSig | control:NumericWritable | 0.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM108 |  |  | Outputs | OaDmprCtrl | control:NumericWritable | 0.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM108 |  |  | Outputs | Or | kitControl:Or | false {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_RM108 |  |  | Overrides | Ov_SpaceTemp | control:NumericWritable | +inf {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM108 |  |  | Overrides | Ov_FanCmd | control:EnumWritable | Auto {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM108 |  |  | Setpoints | DaTempSP | control:NumericWritable | 100.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM108 |  |  | Setpoints | MinDaTempSP | control:NumericWritable | 60.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM108 |  |  | Setpoints | CO2LowLvlSP | control:NumericWritable | 400.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM108 |  |  | Setpoints | CO2HiLvlSP | control:NumericWritable | 1000.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM108 |  |  | Setpoints | OccClgSP | control:NumericWritable | 72.00 {overridden} @ 8
Point | BacnetNetwork | MstpTrunk2 | UV_RM108 |  |  | Setpoints | UnoccClgSP | control:NumericWritable | 85.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM108 |  |  | Setpoints | OccHtgSP | control:NumericWritable | 68.00 {overridden} @ 8
Point | BacnetNetwork | MstpTrunk2 | UV_RM108 |  |  | Setpoints | UnoccHtgSP | control:NumericWritable | 65.00 {overridden} @ 8
Point | BacnetNetwork | MstpTrunk2 | UV_RM108 |  |  | Setpoints | OaClgEnableSP | control:NumericWritable | 55.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM108 |  |  | Setpoints | OaHtgEnableSP | control:NumericWritable | 60.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM108 |  |  | Setpoints | SpaceTempSP | control:NumericWritable | 69.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM108 |  |  | Setpoints | EconMinPosSP | control:NumericWritable | 0.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM108 |  |  | Setpoints | NormalOprFanSpdSp | control:EnumWritable | LoSpd {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM108 |  |  | Setpoints | VRVOprFanSpdSp | control:EnumWritable | HiSpd {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM108 |  |  | Setpoints | FrzstatLatchReset_OS | kitControl:OneShot | false {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_RM108 |  |  | Setpoints | FilterRuntimeRst | control:BooleanWritable | false {ok} @ 10
Point | BacnetNetwork | MstpTrunk2 | UV_RM108 |  |  | Setpoints | FilterRuntimeReset_OS | kitControl:OneShot | false {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_RM108 |  |  | Setpoints | AllowEconOpr | control:BooleanWritable | false {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM108 |  |  | Setpoints | Heating_PID_minAo | control:NumericWritable | 0.10 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM108 |  |  | Setpoints | Heating_PID_maxAo | control:NumericWritable | 0.10 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM108 |  |  | Setpoints | Heating_PID_tr | control:NumericWritable | 10.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM108 |  |  | Network | Schedule | control:BooleanWritable | false {ok} @ 16
Point | BacnetNetwork | MstpTrunk2 | UV_RM108 |  |  | Network | OaTemp | control:NumericWritable | 58.91 {ok} @ 10
Point | BacnetNetwork | MstpTrunk2 | UV_RM108 |  |  | Network | HWSEnable | control:BooleanWritable | true {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM108 |  |  | Network | TextBlock | baja:WsTextBlock | N/A
Point | BacnetNetwork | MstpTrunk2 | UV_RM108 |  |  | Network | OSS | control:BooleanWritable | false {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM108 |  |  | Network | SetReset | kitControl:BqlExprComponent | false | {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_RM108 |  |  | Network | OprModeShare | control:EnumPoint | Fan {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_RM108 |  |  | Network | OptStartStop | vykonPro:OptStartStop | N/A
Point | BacnetNetwork | MstpTrunk2 | UV_RM108 |  |  | Monitoring | EffOcc | control:BooleanPoint | false {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_RM108 |  |  | Monitoring | EffSysEnable | control:BooleanPoint | false {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_RM108 |  |  | Monitoring | EffSpaceSp | control:NumericPoint | 68.00 {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_RM108 |  |  | Monitoring | FilterMaintenanceAlarm | control:BooleanPoint | false {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_RM108 |  |  | Monitoring | EffHeatSP | control:NumericPoint | 65.00 {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_RM108 |  |  | Monitoring | EffCoolSP | control:NumericPoint | 85.00 {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_RM108 |  |  | AV_RandomStartDelay | Proxy Ext | bacnet:BacnetNumericProxyExt | 1.00 | {ok}

## UV_201_EF9
Type | Network | Trunk | Device | Address | DeviceType | PointFolder | PointName | PointType | Value | Status
Point | BacnetNetwork | MstpTrunk2 | UV_201_EF9 |  |  | Inputs | DaTemp | control:NumericPoint | 58.60 {unackedAlarm}
Point | BacnetNetwork | MstpTrunk2 | UV_201_EF9 |  |  | Inputs | SpaceTemp | control:NumericPoint | 65.85 {unackedAlarm}
Point | BacnetNetwork | MstpTrunk2 | UV_201_EF9 |  |  | Inputs | SpaceHumidity | control:NumericPoint | 44.20 {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_201_EF9 |  |  | Inputs | SpaceCO2 | control:NumericPoint | 420.00 {unackedAlarm}
Point | BacnetNetwork | MstpTrunk2 | UV_201_EF9 |  |  | Inputs | SupplyFanSts | control:BooleanPoint | true {unackedAlarm}
Point | BacnetNetwork | MstpTrunk2 | UV_201_EF9 |  |  | Inputs | CFSAlm | control:BooleanPoint | false {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_201_EF9 |  |  | Inputs | GpsSts | control:BooleanPoint | true {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_201_EF9 |  |  | Inputs | HighAlmSp | kitControl:NumericSwitch | 85.00 {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_201_EF9 |  |  | Inputs | Add | kitControl:Add | 88.00 {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_201_EF9 |  |  | Inputs | Subtract | kitControl:Subtract | 62.00 {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_201_EF9 |  |  | Inputs | SpaceTempAlmEnabOfst | control:NumericWritable | 3.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_201_EF9 |  |  | Inputs | SpaceTempAlmDsblDb | control:NumericWritable | 2.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_201_EF9 |  |  | Inputs | LowAlmSp | kitControl:NumericSwitch | 65.00 {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_201_EF9 |  |  | Inputs | Not | kitControl:Not | false {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_201_EF9 |  |  | Inputs | DaTempHiAlmSp | control:NumericWritable | 100.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_201_EF9 |  |  | Inputs | DaTempLoAlmSp | control:NumericWritable | 45.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_201_EF9 |  |  | Inputs | DaTempAlmDsblDb | control:NumericWritable | 3.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_201_EF9 |  |  | Inputs | DxCallForFan | control:BooleanPoint | true {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_201_EF9 |  |  | Outputs | SFLowSpdCmd | control:BooleanPoint | true {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_201_EF9 |  |  | Outputs | SFMedSpdCmd | control:BooleanPoint | false {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_201_EF9 |  |  | Outputs | SFHiSpdCmd | control:BooleanPoint | false {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_201_EF9 |  |  | Outputs | VRVEnable | control:BooleanWritable | false {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_201_EF9 |  |  | Outputs | SteamVlvSig | control:NumericWritable | 0.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_201_EF9 |  |  | Outputs | OaDmprCtrl | control:NumericWritable | 0.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_201_EF9 |  |  | Outputs | Or | kitControl:Or | true {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_201_EF9 |  |  | Overrides | Ov_SpaceTemp | control:NumericWritable | +inf {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_201_EF9 |  |  | Overrides | Ov_FanCmd | control:EnumWritable | Auto {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_201_EF9 |  |  | Setpoints | DaTempSP | control:NumericWritable | 100.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_201_EF9 |  |  | Setpoints | MinDaTempSP | control:NumericWritable | 60.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_201_EF9 |  |  | Setpoints | CO2LowLvlSP | control:NumericWritable | 400.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_201_EF9 |  |  | Setpoints | CO2HiLvlSP | control:NumericWritable | 1000.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_201_EF9 |  |  | Setpoints | OccClgSP | control:NumericWritable | 74.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_201_EF9 |  |  | Setpoints | UnoccClgSP | control:NumericWritable | 85.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_201_EF9 |  |  | Setpoints | OccHtgSP | control:NumericWritable | 70.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_201_EF9 |  |  | Setpoints | UnoccHtgSP | control:NumericWritable | 65.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_201_EF9 |  |  | Setpoints | OaClgEnableSP | control:NumericWritable | 55.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_201_EF9 |  |  | Setpoints | OaHtgEnableSP | control:NumericWritable | 60.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_201_EF9 |  |  | Setpoints | SpaceTempSP | control:NumericWritable | 72.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_201_EF9 |  |  | Setpoints | EconMinPosSP | control:NumericWritable | 0.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_201_EF9 |  |  | Setpoints | NormalOprFanSpdSp | control:EnumWritable | LoSpd {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_201_EF9 |  |  | Setpoints | VRVOprFanSpdSp | control:EnumWritable | HiSpd {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_201_EF9 |  |  | Setpoints | FrzstatLatchReset_OS | kitControl:OneShot | false {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_201_EF9 |  |  | Setpoints | FilterRuntimeRst | control:BooleanWritable | false {ok} @ 10
Point | BacnetNetwork | MstpTrunk2 | UV_201_EF9 |  |  | Setpoints | FilterRuntimeReset_OS | kitControl:OneShot | false {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_201_EF9 |  |  | Setpoints | AllowEconOpr | control:BooleanWritable | false {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_201_EF9 |  |  | Setpoints | Heating_PID_tr | control:NumericWritable | 10.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_201_EF9 |  |  | Setpoints | Heating_PID_maxAo | control:NumericWritable | 0.10 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_201_EF9 |  |  | Setpoints | Heating_PID_minAo | control:NumericWritable | 0.10 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_201_EF9 |  |  | Network | Schedule | control:BooleanWritable | false {ok} @ 16
Point | BacnetNetwork | MstpTrunk2 | UV_201_EF9 |  |  | Network | OaTemp | control:NumericWritable | 58.91 {ok} @ 10
Point | BacnetNetwork | MstpTrunk2 | UV_201_EF9 |  |  | Network | HWSEnable | control:BooleanWritable | true {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_201_EF9 |  |  | Network | TextBlock | baja:WsTextBlock | N/A
Point | BacnetNetwork | MstpTrunk2 | UV_201_EF9 |  |  | Network | OSS | control:BooleanWritable | false {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_201_EF9 |  |  | Network | SetReset | kitControl:BqlExprComponent | false | {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_201_EF9 |  |  | Network | OprModeShare | control:EnumPoint | Fan {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_201_EF9 |  |  | Network | OptStartStop | vykonPro:OptStartStop | N/A
Point | BacnetNetwork | MstpTrunk2 | UV_201_EF9 |  |  | Monitoring | EffOcc | control:BooleanPoint | false {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_201_EF9 |  |  | Monitoring | EffSysEnable | control:BooleanPoint | false {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_201_EF9 |  |  | Monitoring | EffSpaceSp | control:NumericPoint | 70.00 {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_201_EF9 |  |  | Monitoring | FilterMaintenanceAlarm | control:BooleanPoint | false {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_201_EF9 |  |  | Monitoring | EffHeatSP | control:NumericPoint | 65.00 {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_201_EF9 |  |  | Monitoring | EffCoolSP | control:NumericPoint | 85.00 {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_201_EF9 |  |  | EF | EFanSpdSig | control:NumericWritable | 30.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_201_EF9 |  |  | EF | EFanSpdSP | control:NumericWritable | 30.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_201_EF9 |  |  | EF | EFanSts | control:BooleanPoint | false {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_201_EF9 |  |  | EF | EFanCmd | control:BooleanWritable | false {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_201_EF9 |  |  | AV_RandomStartDelay | Proxy Ext | bacnet:BacnetNumericProxyExt | 1.00 | {ok}

## UV_202_EF8
Type | Network | Trunk | Device | Address | DeviceType | PointFolder | PointName | PointType | Value | Status
Point | BacnetNetwork | MstpTrunk2 | UV_202_EF8 |  |  | Inputs | DaTemp | control:NumericPoint | 71.74 {unackedAlarm} alarmInhibit
Point | BacnetNetwork | MstpTrunk2 | UV_202_EF8 |  |  | Inputs | SpaceTemp | control:NumericPoint | 70.69 {unackedAlarm}
Point | BacnetNetwork | MstpTrunk2 | UV_202_EF8 |  |  | Inputs | SpaceHumidity | control:NumericPoint | 36.98 {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_202_EF8 |  |  | Inputs | SpaceCO2 | control:NumericPoint | 425.00 {unackedAlarm}
Point | BacnetNetwork | MstpTrunk2 | UV_202_EF8 |  |  | Inputs | SupplyFanSts | control:BooleanPoint | false {unackedAlarm}
Point | BacnetNetwork | MstpTrunk2 | UV_202_EF8 |  |  | Inputs | CFSAlm | control:BooleanPoint | false {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_202_EF8 |  |  | Inputs | GpsSts | control:BooleanPoint | true {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_202_EF8 |  |  | Inputs | HighAlmSp | kitControl:NumericSwitch | 85.00 {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_202_EF8 |  |  | Inputs | Add | kitControl:Add | 88.00 {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_202_EF8 |  |  | Inputs | Subtract | kitControl:Subtract | 62.00 {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_202_EF8 |  |  | Inputs | SpaceTempAlmEnabOfst | control:NumericWritable | 3.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_202_EF8 |  |  | Inputs | SpaceTempAlmDsblDb | control:NumericWritable | 2.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_202_EF8 |  |  | Inputs | LowAlmSp | kitControl:NumericSwitch | 65.00 {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_202_EF8 |  |  | Inputs | Not | kitControl:Not | true {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_202_EF8 |  |  | Inputs | DaTempHiAlmSp | control:NumericWritable | 100.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_202_EF8 |  |  | Inputs | DaTempLoAlmSp | control:NumericWritable | 45.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_202_EF8 |  |  | Inputs | DaTempAlmDsblDb | control:NumericWritable | 3.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_202_EF8 |  |  | Inputs | DxCallForFan | control:BooleanPoint | false {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_202_EF8 |  |  | Outputs | SFLowSpdCmd | control:BooleanPoint | false {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_202_EF8 |  |  | Outputs | SFMedSpdCmd | control:BooleanPoint | false {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_202_EF8 |  |  | Outputs | SFHiSpdCmd | control:BooleanPoint | false {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_202_EF8 |  |  | Outputs | VRVEnable | control:BooleanWritable | false {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_202_EF8 |  |  | Outputs | SteamVlvSig | control:NumericWritable | 0.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_202_EF8 |  |  | Outputs | OaDmprCtrl | control:NumericWritable | 0.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_202_EF8 |  |  | Outputs | Or | kitControl:Or | false {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_202_EF8 |  |  | Overrides | Ov_SpaceTemp | control:NumericWritable | +inf {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_202_EF8 |  |  | Overrides | Ov_FanCmd | control:EnumWritable | Auto {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_202_EF8 |  |  | Setpoints | DaTempSP | control:NumericWritable | 100.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_202_EF8 |  |  | Setpoints | MinDaTempSP | control:NumericWritable | 60.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_202_EF8 |  |  | Setpoints | CO2LowLvlSP | control:NumericWritable | 400.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_202_EF8 |  |  | Setpoints | CO2HiLvlSP | control:NumericWritable | 1000.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_202_EF8 |  |  | Setpoints | OccClgSP | control:NumericWritable | 74.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_202_EF8 |  |  | Setpoints | UnoccClgSP | control:NumericWritable | 85.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_202_EF8 |  |  | Setpoints | OccHtgSP | control:NumericWritable | 70.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_202_EF8 |  |  | Setpoints | UnoccHtgSP | control:NumericWritable | 65.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_202_EF8 |  |  | Setpoints | OaClgEnableSP | control:NumericWritable | 55.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_202_EF8 |  |  | Setpoints | OaHtgEnableSP | control:NumericWritable | 60.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_202_EF8 |  |  | Setpoints | SpaceTempSP | control:NumericWritable | 72.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_202_EF8 |  |  | Setpoints | EconMinPosSP | control:NumericWritable | 0.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_202_EF8 |  |  | Setpoints | NormalOprFanSpdSp | control:EnumWritable | LoSpd {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_202_EF8 |  |  | Setpoints | VRVOprFanSpdSp | control:EnumWritable | HiSpd {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_202_EF8 |  |  | Setpoints | FrzstatLatchReset_OS | kitControl:OneShot | false {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_202_EF8 |  |  | Setpoints | FilterRuntimeRst | control:BooleanWritable | false {ok} @ 10
Point | BacnetNetwork | MstpTrunk2 | UV_202_EF8 |  |  | Setpoints | FilterRuntimeReset_OS | kitControl:OneShot | false {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_202_EF8 |  |  | Setpoints | AllowEconOpr | control:BooleanWritable | false {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_202_EF8 |  |  | Setpoints | Heating_PID_tr | control:NumericWritable | 10.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_202_EF8 |  |  | Setpoints | Heating_PID_maxAo | control:NumericWritable | 0.10 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_202_EF8 |  |  | Setpoints | Heating_PID_minAo | control:NumericWritable | 0.10 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_202_EF8 |  |  | Network | Schedule | control:BooleanWritable | false {ok} @ 16
Point | BacnetNetwork | MstpTrunk2 | UV_202_EF8 |  |  | Network | OaTemp | control:NumericWritable | 58.91 {ok} @ 10
Point | BacnetNetwork | MstpTrunk2 | UV_202_EF8 |  |  | Network | HWSEnable | control:BooleanWritable | true {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_202_EF8 |  |  | Network | TextBlock | baja:WsTextBlock | N/A
Point | BacnetNetwork | MstpTrunk2 | UV_202_EF8 |  |  | Network | OSS | control:BooleanWritable | false {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_202_EF8 |  |  | Network | SetReset | kitControl:BqlExprComponent | false | {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_202_EF8 |  |  | Network | OprModeShare | control:EnumPoint | Fan {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_202_EF8 |  |  | Network | OptStartStop | vykonPro:OptStartStop | N/A
Point | BacnetNetwork | MstpTrunk2 | UV_202_EF8 |  |  | Monitoring | EffOcc | control:BooleanPoint | false {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_202_EF8 |  |  | Monitoring | EffSysEnable | control:BooleanPoint | false {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_202_EF8 |  |  | Monitoring | EffSpaceSp | control:NumericPoint | 70.00 {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_202_EF8 |  |  | Monitoring | FilterMaintenanceAlarm | control:BooleanPoint | false {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_202_EF8 |  |  | Monitoring | EffHeatSP | control:NumericPoint | 65.00 {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_202_EF8 |  |  | Monitoring | EffCoolSP | control:NumericPoint | 85.00 {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_202_EF8 |  |  | EF | EFanSpdSig | control:NumericWritable | 0.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_202_EF8 |  |  | EF | EFanSpdSP | control:NumericWritable | 30.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_202_EF8 |  |  | EF | EFanSts | control:BooleanPoint | false {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_202_EF8 |  |  | EF | EFanCmd | control:BooleanWritable | false {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_202_EF8 |  |  | AV_RandomStartDelay | Proxy Ext | bacnet:BacnetNumericProxyExt | 1.00 | {ok}

## UV_RM203
Type | Network | Trunk | Device | Address | DeviceType | PointFolder | PointName | PointType | Value | Status
Point | BacnetNetwork | MstpTrunk2 | UV_RM203 |  |  | Inputs | DaTemp | control:NumericPoint | 73.68 {unackedAlarm} alarmInhibit
Point | BacnetNetwork | MstpTrunk2 | UV_RM203 |  |  | Inputs | SpaceTemp | control:NumericPoint | 70.70 {unackedAlarm}
Point | BacnetNetwork | MstpTrunk2 | UV_RM203 |  |  | Inputs | SpaceHumidity | control:NumericPoint | 42.36 {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_RM203 |  |  | Inputs | SpaceCO2 | control:NumericPoint | 414.00 {unackedAlarm}
Point | BacnetNetwork | MstpTrunk2 | UV_RM203 |  |  | Inputs | SupplyFanSts | control:BooleanPoint | false {unackedAlarm}
Point | BacnetNetwork | MstpTrunk2 | UV_RM203 |  |  | Inputs | CFSAlm | control:BooleanPoint | false {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_RM203 |  |  | Inputs | GpsSts | control:BooleanPoint | true {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_RM203 |  |  | Inputs | HighAlmSp | kitControl:NumericSwitch | 85.00 {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_RM203 |  |  | Inputs | Add | kitControl:Add | 88.00 {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_RM203 |  |  | Inputs | Subtract | kitControl:Subtract | 52.00 {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_RM203 |  |  | Inputs | SpaceTempAlmEnabOfst | control:NumericWritable | 3.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM203 |  |  | Inputs | SpaceTempAlmDsblDb | control:NumericWritable | 2.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM203 |  |  | Inputs | LowAlmSp | kitControl:NumericSwitch | 55.00 {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_RM203 |  |  | Inputs | Not | kitControl:Not | true {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_RM203 |  |  | Inputs | DaTempHiAlmSp | control:NumericWritable | 100.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM203 |  |  | Inputs | DaTempLoAlmSp | control:NumericWritable | 45.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM203 |  |  | Inputs | DaTempAlmDsblDb | control:NumericWritable | 3.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM203 |  |  | Inputs | DxCallForFan | control:BooleanPoint | false {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_RM203 |  |  | Outputs | SFLowSpdCmd | control:BooleanPoint | false {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_RM203 |  |  | Outputs | SFMedSpdCmd | control:BooleanPoint | false {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_RM203 |  |  | Outputs | SFHiSpdCmd | control:BooleanPoint | false {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_RM203 |  |  | Outputs | VRVEnable | control:BooleanWritable | false {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM203 |  |  | Outputs | SteamVlvSig | control:NumericWritable | 0.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM203 |  |  | Outputs | OaDmprCtrl | control:NumericWritable | 0.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM203 |  |  | Outputs | Or | kitControl:Or | false {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_RM203 |  |  | Overrides | Ov_SpaceTemp | control:NumericWritable | +inf {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM203 |  |  | Overrides | Ov_FanCmd | control:EnumWritable | Auto {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM203 |  |  | Setpoints | DaTempSP | control:NumericWritable | 100.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM203 |  |  | Setpoints | MinDaTempSP | control:NumericWritable | 60.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM203 |  |  | Setpoints | CO2LowLvlSP | control:NumericWritable | 400.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM203 |  |  | Setpoints | CO2HiLvlSP | control:NumericWritable | 1000.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM203 |  |  | Setpoints | OccClgSP | control:NumericWritable | 74.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM203 |  |  | Setpoints | UnoccClgSP | control:NumericWritable | 85.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM203 |  |  | Setpoints | OccHtgSP | control:NumericWritable | 70.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM203 |  |  | Setpoints | UnoccHtgSP | control:NumericWritable | 55.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM203 |  |  | Setpoints | OaClgEnableSP | control:NumericWritable | 55.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM203 |  |  | Setpoints | OaHtgEnableSP | control:NumericWritable | 60.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM203 |  |  | Setpoints | SpaceTempSP | control:NumericWritable | 69.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM203 |  |  | Setpoints | EconMinPosSP | control:NumericWritable | 0.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM203 |  |  | Setpoints | NormalOprFanSpdSp | control:EnumWritable | LoSpd {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM203 |  |  | Setpoints | VRVOprFanSpdSp | control:EnumWritable | HiSpd {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM203 |  |  | Setpoints | FrzstatLatchReset_OS | kitControl:OneShot | false {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_RM203 |  |  | Setpoints | FilterRuntimeRst | control:BooleanWritable | false {ok} @ 10
Point | BacnetNetwork | MstpTrunk2 | UV_RM203 |  |  | Setpoints | FilterRuntimeReset_OS | kitControl:OneShot | false {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_RM203 |  |  | Setpoints | AllowEconOpr | control:BooleanWritable | false {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM203 |  |  | Setpoints | Heating_PID_tr | control:NumericWritable | 10.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM203 |  |  | Setpoints | Heating_PID_maxAo | control:NumericWritable | 0.10 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM203 |  |  | Setpoints | Heating_PID_minAo | control:NumericWritable | 0.10 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM203 |  |  | Network | Schedule | control:BooleanWritable | false {ok} @ 16
Point | BacnetNetwork | MstpTrunk2 | UV_RM203 |  |  | Network | OaTemp | control:NumericWritable | 58.91 {ok} @ 10
Point | BacnetNetwork | MstpTrunk2 | UV_RM203 |  |  | Network | HWSEnable | control:BooleanWritable | true {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM203 |  |  | Network | TextBlock | baja:WsTextBlock | N/A
Point | BacnetNetwork | MstpTrunk2 | UV_RM203 |  |  | Network | OSS | control:BooleanWritable | false {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM203 |  |  | Network | SetReset | kitControl:BqlExprComponent | false | {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_RM203 |  |  | Network | OprModeShare | control:EnumPoint | Fan {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_RM203 |  |  | Network | OptStartStop | vykonPro:OptStartStop | N/A
Point | BacnetNetwork | MstpTrunk2 | UV_RM203 |  |  | Monitoring | EffOcc | control:BooleanPoint | false {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_RM203 |  |  | Monitoring | EffSysEnable | control:BooleanPoint | false {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_RM203 |  |  | Monitoring | EffSpaceSp | control:NumericPoint | 70.00 {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_RM203 |  |  | Monitoring | FilterMaintenanceAlarm | control:BooleanPoint | false {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_RM203 |  |  | Monitoring | EffHeatSP | control:NumericPoint | 55.00 {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_RM203 |  |  | Monitoring | EffCoolSP | control:NumericPoint | 85.00 {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_RM203 |  |  | AV_RandomStartDelay | Proxy Ext | bacnet:BacnetNumericProxyExt | 1.00 | {ok}

## UV_RM204
Type | Network | Trunk | Device | Address | DeviceType | PointFolder | PointName | PointType | Value | Status
Point | BacnetNetwork | MstpTrunk2 | UV_RM204 |  |  | Inputs | DaTemp | control:NumericPoint | 73.85 {unackedAlarm} alarmInhibit
Point | BacnetNetwork | MstpTrunk2 | UV_RM204 |  |  | Inputs | SpaceTemp | control:NumericPoint | 71.12 {unackedAlarm}
Point | BacnetNetwork | MstpTrunk2 | UV_RM204 |  |  | Inputs | SpaceHumidity | control:NumericPoint | 36.26 {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_RM204 |  |  | Inputs | SpaceCO2 | control:NumericPoint | 413.00 {unackedAlarm}
Point | BacnetNetwork | MstpTrunk2 | UV_RM204 |  |  | Inputs | SupplyFanSts | control:BooleanPoint | false {unackedAlarm}
Point | BacnetNetwork | MstpTrunk2 | UV_RM204 |  |  | Inputs | CFSAlm | control:BooleanPoint | false {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_RM204 |  |  | Inputs | GpsSts | control:BooleanPoint | true {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_RM204 |  |  | Inputs | HighAlmSp | kitControl:NumericSwitch | 85.00 {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_RM204 |  |  | Inputs | Add | kitControl:Add | 88.00 {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_RM204 |  |  | Inputs | Subtract | kitControl:Subtract | 62.00 {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_RM204 |  |  | Inputs | SpaceTempAlmEnabOfst | control:NumericWritable | 3.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM204 |  |  | Inputs | SpaceTempAlmDsblDb | control:NumericWritable | 2.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM204 |  |  | Inputs | LowAlmSp | kitControl:NumericSwitch | 65.00 {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_RM204 |  |  | Inputs | Not | kitControl:Not | true {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_RM204 |  |  | Inputs | DaTempHiAlmSp | control:NumericWritable | 100.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM204 |  |  | Inputs | DaTempLoAlmSp | control:NumericWritable | 45.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM204 |  |  | Inputs | DaTempAlmDsblDb | control:NumericWritable | 3.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM204 |  |  | Inputs | DxCallForFan | control:BooleanPoint | false {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_RM204 |  |  | Outputs | SFLowSpdCmd | control:BooleanPoint | false {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_RM204 |  |  | Outputs | SFMedSpdCmd | control:BooleanPoint | false {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_RM204 |  |  | Outputs | SFHiSpdCmd | control:BooleanPoint | false {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_RM204 |  |  | Outputs | VRVEnable | control:BooleanWritable | false {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM204 |  |  | Outputs | SteamVlvSig | control:NumericWritable | 0.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM204 |  |  | Outputs | OaDmprCtrl | control:NumericWritable | 0.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM204 |  |  | Outputs | Or | kitControl:Or | false {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_RM204 |  |  | Overrides | Ov_SpaceTemp | control:NumericWritable | +inf {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM204 |  |  | Overrides | Ov_FanCmd | control:EnumWritable | Auto {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM204 |  |  | Setpoints | DaTempSP | control:NumericWritable | 100.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM204 |  |  | Setpoints | MinDaTempSP | control:NumericWritable | 60.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM204 |  |  | Setpoints | CO2LowLvlSP | control:NumericWritable | 400.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM204 |  |  | Setpoints | CO2HiLvlSP | control:NumericWritable | 1000.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM204 |  |  | Setpoints | OccClgSP | control:NumericWritable | 74.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM204 |  |  | Setpoints | UnoccClgSP | control:NumericWritable | 85.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM204 |  |  | Setpoints | OccHtgSP | control:NumericWritable | 70.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM204 |  |  | Setpoints | UnoccHtgSP | control:NumericWritable | 65.00 {overridden} @ 8
Point | BacnetNetwork | MstpTrunk2 | UV_RM204 |  |  | Setpoints | OaClgEnableSP | control:NumericWritable | 55.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM204 |  |  | Setpoints | OaHtgEnableSP | control:NumericWritable | 60.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM204 |  |  | Setpoints | SpaceTempSP | control:NumericWritable | 72.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM204 |  |  | Setpoints | EconMinPosSP | control:NumericWritable | 0.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM204 |  |  | Setpoints | NormalOprFanSpdSp | control:EnumWritable | LoSpd {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM204 |  |  | Setpoints | VRVOprFanSpdSp | control:EnumWritable | HiSpd {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM204 |  |  | Setpoints | FrzstatLatchReset_OS | kitControl:OneShot | false {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_RM204 |  |  | Setpoints | FilterRuntimeRst | control:BooleanWritable | false {ok} @ 10
Point | BacnetNetwork | MstpTrunk2 | UV_RM204 |  |  | Setpoints | FilterRuntimeReset_OS | kitControl:OneShot | false {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_RM204 |  |  | Setpoints | AllowEconOpr | control:BooleanWritable | false {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM204 |  |  | Setpoints | Heating_PID_tr | control:NumericWritable | 10.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM204 |  |  | Setpoints | Heating_PID_maxAo | control:NumericWritable | 0.10 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM204 |  |  | Setpoints | Heating_PID_minAo | control:NumericWritable | 0.10 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM204 |  |  | Network | Schedule | control:BooleanWritable | false {ok} @ 16
Point | BacnetNetwork | MstpTrunk2 | UV_RM204 |  |  | Network | OaTemp | control:NumericWritable | 58.91 {ok} @ 10
Point | BacnetNetwork | MstpTrunk2 | UV_RM204 |  |  | Network | HWSEnable | control:BooleanWritable | true {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM204 |  |  | Network | TextBlock | baja:WsTextBlock | N/A
Point | BacnetNetwork | MstpTrunk2 | UV_RM204 |  |  | Network | OSS | control:BooleanWritable | false {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM204 |  |  | Network | SetReset | kitControl:BqlExprComponent | false | {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_RM204 |  |  | Network | OprModeShare | control:EnumPoint | Fan {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_RM204 |  |  | Network | OptStartStop | vykonPro:OptStartStop | N/A
Point | BacnetNetwork | MstpTrunk2 | UV_RM204 |  |  | Monitoring | EffOcc | control:BooleanPoint | false {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_RM204 |  |  | Monitoring | EffSysEnable | control:BooleanPoint | false {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_RM204 |  |  | Monitoring | EffSpaceSp | control:NumericPoint | 70.00 {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_RM204 |  |  | Monitoring | FilterMaintenanceAlarm | control:BooleanPoint | false {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_RM204 |  |  | Monitoring | EffHeatSP | control:NumericPoint | 65.00 {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_RM204 |  |  | Monitoring | EffCoolSP | control:NumericPoint | 85.00 {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_RM204 |  |  | AV_RandomStartDelay | Proxy Ext | bacnet:BacnetNumericProxyExt | 1.00 | {ok}

## UV_RM205
Type | Network | Trunk | Device | Address | DeviceType | PointFolder | PointName | PointType | Value | Status
Point | BacnetNetwork | MstpTrunk2 | UV_RM205 |  |  | Inputs | DaTemp | control:NumericPoint | 75.72 {unackedAlarm} alarmInhibit
Point | BacnetNetwork | MstpTrunk2 | UV_RM205 |  |  | Inputs | SpaceTemp | control:NumericPoint | 72.83 {unackedAlarm}
Point | BacnetNetwork | MstpTrunk2 | UV_RM205 |  |  | Inputs | SpaceHumidity | control:NumericPoint | 34.22 {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_RM205 |  |  | Inputs | SpaceCO2 | control:NumericPoint | 412.00 {unackedAlarm}
Point | BacnetNetwork | MstpTrunk2 | UV_RM205 |  |  | Inputs | SupplyFanSts | control:BooleanPoint | false {unackedAlarm}
Point | BacnetNetwork | MstpTrunk2 | UV_RM205 |  |  | Inputs | CFSAlm | control:BooleanPoint | false {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_RM205 |  |  | Inputs | GpsSts | control:BooleanPoint | true {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_RM205 |  |  | Inputs | HighAlmSp | kitControl:NumericSwitch | 85.00 {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_RM205 |  |  | Inputs | Add | kitControl:Add | 88.00 {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_RM205 |  |  | Inputs | Subtract | kitControl:Subtract | 62.00 {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_RM205 |  |  | Inputs | SpaceTempAlmEnabOfst | control:NumericWritable | 3.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM205 |  |  | Inputs | SpaceTempAlmDsblDb | control:NumericWritable | 2.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM205 |  |  | Inputs | LowAlmSp | kitControl:NumericSwitch | 65.00 {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_RM205 |  |  | Inputs | Not | kitControl:Not | true {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_RM205 |  |  | Inputs | DaTempHiAlmSp | control:NumericWritable | 100.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM205 |  |  | Inputs | DaTempLoAlmSp | control:NumericWritable | 45.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM205 |  |  | Inputs | DaTempAlmDsblDb | control:NumericWritable | 3.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM205 |  |  | Inputs | DxCallForFan | control:BooleanPoint | false {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_RM205 |  |  | Outputs | SFLowSpdCmd | control:BooleanPoint | false {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_RM205 |  |  | Outputs | SFMedSpdCmd | control:BooleanPoint | false {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_RM205 |  |  | Outputs | SFHiSpdCmd | control:BooleanPoint | false {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_RM205 |  |  | Outputs | VRVEnable | control:BooleanWritable | false {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM205 |  |  | Outputs | SteamVlvSig | control:NumericWritable | 0.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM205 |  |  | Outputs | OaDmprCtrl | control:NumericWritable | 0.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM205 |  |  | Outputs | Or | kitControl:Or | false {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_RM205 |  |  | Overrides | Ov_SpaceTemp | control:NumericWritable | +inf {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM205 |  |  | Overrides | Ov_FanCmd | control:EnumWritable | Auto {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM205 |  |  | Setpoints | DaTempSP | control:NumericWritable | 100.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM205 |  |  | Setpoints | MinDaTempSP | control:NumericWritable | 60.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM205 |  |  | Setpoints | CO2LowLvlSP | control:NumericWritable | 400.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM205 |  |  | Setpoints | CO2HiLvlSP | control:NumericWritable | 1000.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM205 |  |  | Setpoints | OccClgSP | control:NumericWritable | 74.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM205 |  |  | Setpoints | UnoccClgSP | control:NumericWritable | 85.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM205 |  |  | Setpoints | OccHtgSP | control:NumericWritable | 70.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM205 |  |  | Setpoints | UnoccHtgSP | control:NumericWritable | 65.00 {overridden} @ 8
Point | BacnetNetwork | MstpTrunk2 | UV_RM205 |  |  | Setpoints | OaClgEnableSP | control:NumericWritable | 55.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM205 |  |  | Setpoints | OaHtgEnableSP | control:NumericWritable | 60.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM205 |  |  | Setpoints | SpaceTempSP | control:NumericWritable | 72.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM205 |  |  | Setpoints | EconMinPosSP | control:NumericWritable | 0.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM205 |  |  | Setpoints | NormalOprFanSpdSp | control:EnumWritable | LoSpd {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM205 |  |  | Setpoints | VRVOprFanSpdSp | control:EnumWritable | HiSpd {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM205 |  |  | Setpoints | FrzstatLatchReset_OS | kitControl:OneShot | false {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_RM205 |  |  | Setpoints | FilterRuntimeRst | control:BooleanWritable | false {ok} @ 10
Point | BacnetNetwork | MstpTrunk2 | UV_RM205 |  |  | Setpoints | FilterRuntimeReset_OS | kitControl:OneShot | false {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_RM205 |  |  | Setpoints | AllowEconOpr | control:BooleanWritable | false {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM205 |  |  | Setpoints | Heating_PID_tr | control:NumericWritable | 10.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM205 |  |  | Setpoints | Heating_PID_maxAo | control:NumericWritable | 0.10 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM205 |  |  | Setpoints | Heating_PID_minAo | control:NumericWritable | 0.10 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM205 |  |  | Network | Schedule | control:BooleanWritable | false {ok} @ 16
Point | BacnetNetwork | MstpTrunk2 | UV_RM205 |  |  | Network | OaTemp | control:NumericWritable | 58.91 {ok} @ 10
Point | BacnetNetwork | MstpTrunk2 | UV_RM205 |  |  | Network | HWSEnable | control:BooleanWritable | true {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM205 |  |  | Network | TextBlock | baja:WsTextBlock | N/A
Point | BacnetNetwork | MstpTrunk2 | UV_RM205 |  |  | Network | OSS | control:BooleanWritable | false {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM205 |  |  | Network | SetReset | kitControl:BqlExprComponent | false | {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_RM205 |  |  | Network | OprModeShare | control:EnumPoint | Fan {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_RM205 |  |  | Network | OptStartStop | vykonPro:OptStartStop | N/A
Point | BacnetNetwork | MstpTrunk2 | UV_RM205 |  |  | Monitoring | EffOcc | control:BooleanPoint | false {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_RM205 |  |  | Monitoring | EffSysEnable | control:BooleanPoint | false {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_RM205 |  |  | Monitoring | EffSpaceSp | control:NumericPoint | 70.00 {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_RM205 |  |  | Monitoring | FilterMaintenanceAlarm | control:BooleanPoint | false {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_RM205 |  |  | Monitoring | EffHeatSP | control:NumericPoint | 65.00 {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_RM205 |  |  | Monitoring | EffCoolSP | control:NumericPoint | 85.00 {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_RM205 |  |  | AV_RandomStartDelay | Proxy Ext | bacnet:BacnetNumericProxyExt | 1.00 | {ok}

## UV_206_EF7
Type | Network | Trunk | Device | Address | DeviceType | PointFolder | PointName | PointType | Value | Status
Point | BacnetNetwork | MstpTrunk2 | UV_206_EF7 |  |  | Inputs | DaTemp | control:NumericPoint | 75.00 {unackedAlarm} alarmInhibit
Point | BacnetNetwork | MstpTrunk2 | UV_206_EF7 |  |  | Inputs | SpaceTemp | control:NumericPoint | 72.57 {unackedAlarm}
Point | BacnetNetwork | MstpTrunk2 | UV_206_EF7 |  |  | Inputs | SpaceHumidity | control:NumericPoint | 36.24 {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_206_EF7 |  |  | Inputs | SpaceCO2 | control:NumericPoint | 428.00 {unackedAlarm}
Point | BacnetNetwork | MstpTrunk2 | UV_206_EF7 |  |  | Inputs | SupplyFanSts | control:BooleanPoint | false {unackedAlarm}
Point | BacnetNetwork | MstpTrunk2 | UV_206_EF7 |  |  | Inputs | CFSAlm | control:BooleanPoint | false {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_206_EF7 |  |  | Inputs | GpsSts | control:BooleanPoint | true {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_206_EF7 |  |  | Inputs | HighAlmSp | kitControl:NumericSwitch | 85.00 {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_206_EF7 |  |  | Inputs | Add | kitControl:Add | 88.00 {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_206_EF7 |  |  | Inputs | Subtract | kitControl:Subtract | 62.00 {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_206_EF7 |  |  | Inputs | SpaceTempAlmEnabOfst | control:NumericWritable | 3.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_206_EF7 |  |  | Inputs | SpaceTempAlmDsblDb | control:NumericWritable | 2.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_206_EF7 |  |  | Inputs | LowAlmSp | kitControl:NumericSwitch | 65.00 {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_206_EF7 |  |  | Inputs | Not | kitControl:Not | true {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_206_EF7 |  |  | Inputs | DaTempHiAlmSp | control:NumericWritable | 100.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_206_EF7 |  |  | Inputs | DaTempLoAlmSp | control:NumericWritable | 45.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_206_EF7 |  |  | Inputs | DaTempAlmDsblDb | control:NumericWritable | 3.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_206_EF7 |  |  | Inputs | DxCallForFan | control:BooleanPoint | false {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_206_EF7 |  |  | Outputs | SFLowSpdCmd | control:BooleanPoint | false {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_206_EF7 |  |  | Outputs | SFMedSpdCmd | control:BooleanPoint | false {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_206_EF7 |  |  | Outputs | SFHiSpdCmd | control:BooleanPoint | false {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_206_EF7 |  |  | Outputs | VRVEnable | control:BooleanWritable | false {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_206_EF7 |  |  | Outputs | SteamVlvSig | control:NumericWritable | 0.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_206_EF7 |  |  | Outputs | OaDmprCtrl | control:NumericWritable | 0.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_206_EF7 |  |  | Outputs | Or | kitControl:Or | false {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_206_EF7 |  |  | Overrides | Ov_SpaceTemp | control:NumericWritable | +inf {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_206_EF7 |  |  | Overrides | Ov_FanCmd | control:EnumWritable | Auto {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_206_EF7 |  |  | Setpoints | DaTempSP | control:NumericWritable | 100.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_206_EF7 |  |  | Setpoints | MinDaTempSP | control:NumericWritable | 60.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_206_EF7 |  |  | Setpoints | CO2LowLvlSP | control:NumericWritable | 400.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_206_EF7 |  |  | Setpoints | CO2HiLvlSP | control:NumericWritable | 1000.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_206_EF7 |  |  | Setpoints | OccClgSP | control:NumericWritable | 74.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_206_EF7 |  |  | Setpoints | UnoccClgSP | control:NumericWritable | 85.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_206_EF7 |  |  | Setpoints | OccHtgSP | control:NumericWritable | 68.00 {overridden} @ 8
Point | BacnetNetwork | MstpTrunk2 | UV_206_EF7 |  |  | Setpoints | UnoccHtgSP | control:NumericWritable | 65.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_206_EF7 |  |  | Setpoints | OaClgEnableSP | control:NumericWritable | 55.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_206_EF7 |  |  | Setpoints | OaHtgEnableSP | control:NumericWritable | 60.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_206_EF7 |  |  | Setpoints | SpaceTempSP | control:NumericWritable | 72.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_206_EF7 |  |  | Setpoints | EconMinPosSP | control:NumericWritable | 0.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_206_EF7 |  |  | Setpoints | NormalOprFanSpdSp | control:EnumWritable | LoSpd {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_206_EF7 |  |  | Setpoints | VRVOprFanSpdSp | control:EnumWritable | HiSpd {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_206_EF7 |  |  | Setpoints | FrzstatLatchReset_OS | kitControl:OneShot | false {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_206_EF7 |  |  | Setpoints | FilterRuntimeRst | control:BooleanWritable | false {ok} @ 10
Point | BacnetNetwork | MstpTrunk2 | UV_206_EF7 |  |  | Setpoints | FilterRuntimeReset_OS | kitControl:OneShot | false {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_206_EF7 |  |  | Setpoints | AllowEconOpr | control:BooleanWritable | false {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_206_EF7 |  |  | Setpoints | Heating_PID_tr | control:NumericWritable | 10.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_206_EF7 |  |  | Setpoints | Heating_PID_maxAo | control:NumericWritable | 0.10 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_206_EF7 |  |  | Setpoints | Heating_PID_minAo | control:NumericWritable | 0.10 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_206_EF7 |  |  | Network | Schedule | control:BooleanWritable | false {ok} @ 16
Point | BacnetNetwork | MstpTrunk2 | UV_206_EF7 |  |  | Network | TextBlock | baja:WsTextBlock | N/A
Point | BacnetNetwork | MstpTrunk2 | UV_206_EF7 |  |  | Network | SetReset | kitControl:BqlExprComponent | false | {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_206_EF7 |  |  | Network | OprModeShare | control:EnumPoint | Fan {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_206_EF7 |  |  | Network | OptStartStop | vykonPro:OptStartStop | N/A
Point | BacnetNetwork | MstpTrunk2 | UV_206_EF7 |  |  | Network | OaTemp | control:NumericWritable | 58.91 {ok} @ 10
Point | BacnetNetwork | MstpTrunk2 | UV_206_EF7 |  |  | Network | HWSEnable | control:BooleanWritable | true {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_206_EF7 |  |  | Network | OSS | control:BooleanWritable | false {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_206_EF7 |  |  | Monitoring | EffOcc | control:BooleanPoint | false {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_206_EF7 |  |  | Monitoring | EffSysEnable | control:BooleanPoint | false {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_206_EF7 |  |  | Monitoring | EffSpaceSp | control:NumericPoint | 68.00 {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_206_EF7 |  |  | Monitoring | FilterMaintenanceAlarm | control:BooleanPoint | false {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_206_EF7 |  |  | Monitoring | EffHeatSP | control:NumericPoint | 65.00 {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_206_EF7 |  |  | Monitoring | EffCoolSP | control:NumericPoint | 85.00 {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_206_EF7 |  |  | EF | EFanSpdSig | control:NumericWritable | +inf {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_206_EF7 |  |  | EF | EFanSpdSP | control:NumericWritable | 30.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_206_EF7 |  |  | EF | EFanSts | control:BooleanPoint | false {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_206_EF7 |  |  | EF | EFanCmd | control:BooleanWritable | false {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_206_EF7 |  |  | AV_RandomStartDelay | Proxy Ext | bacnet:BacnetNumericProxyExt | 1.00 | {ok}

## UV_207_EF10
Type | Network | Trunk | Device | Address | DeviceType | PointFolder | PointName | PointType | Value | Status
Point | BacnetNetwork | MstpTrunk2 | UV_207_EF10 |  |  | Inputs | DaTemp | control:NumericPoint | 75.98 {unackedAlarm} alarmInhibit
Point | BacnetNetwork | MstpTrunk2 | UV_207_EF10 |  |  | Inputs | SpaceTemp | control:NumericPoint | 73.01 {unackedAlarm}
Point | BacnetNetwork | MstpTrunk2 | UV_207_EF10 |  |  | Inputs | SpaceHumidity | control:NumericPoint | 30.13 {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_207_EF10 |  |  | Inputs | SpaceCO2 | control:NumericPoint | 400.00 {unackedAlarm}
Point | BacnetNetwork | MstpTrunk2 | UV_207_EF10 |  |  | Inputs | SupplyFanSts | control:BooleanPoint | false {unackedAlarm}
Point | BacnetNetwork | MstpTrunk2 | UV_207_EF10 |  |  | Inputs | CFSAlm | control:BooleanPoint | false {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_207_EF10 |  |  | Inputs | GpsSts | control:BooleanPoint | true {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_207_EF10 |  |  | Inputs | HighAlmSp | kitControl:NumericSwitch | 85.00 {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_207_EF10 |  |  | Inputs | Add | kitControl:Add | 88.00 {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_207_EF10 |  |  | Inputs | Subtract | kitControl:Subtract | 62.00 {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_207_EF10 |  |  | Inputs | SpaceTempAlmEnabOfst | control:NumericWritable | 3.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_207_EF10 |  |  | Inputs | SpaceTempAlmDsblDb | control:NumericWritable | 2.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_207_EF10 |  |  | Inputs | LowAlmSp | kitControl:NumericSwitch | 65.00 {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_207_EF10 |  |  | Inputs | Not | kitControl:Not | true {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_207_EF10 |  |  | Inputs | DaTempHiAlmSp | control:NumericWritable | 100.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_207_EF10 |  |  | Inputs | DaTempLoAlmSp | control:NumericWritable | 45.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_207_EF10 |  |  | Inputs | DaTempAlmDsblDb | control:NumericWritable | 3.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_207_EF10 |  |  | Inputs | DxCallForFan | control:BooleanPoint | false {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_207_EF10 |  |  | Outputs | SFLowSpdCmd | control:BooleanPoint | false {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_207_EF10 |  |  | Outputs | SFMedSpdCmd | control:BooleanPoint | false {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_207_EF10 |  |  | Outputs | SFHiSpdCmd | control:BooleanPoint | false {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_207_EF10 |  |  | Outputs | VRVEnable | control:BooleanWritable | false {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_207_EF10 |  |  | Outputs | SteamVlvSig | control:NumericWritable | 0.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_207_EF10 |  |  | Outputs | OaDmprCtrl | control:NumericWritable | 0.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_207_EF10 |  |  | Outputs | Or | kitControl:Or | false {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_207_EF10 |  |  | Overrides | Ov_SpaceTemp | control:NumericWritable | +inf {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_207_EF10 |  |  | Overrides | Ov_FanCmd | control:EnumWritable | Auto {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_207_EF10 |  |  | Setpoints | DaTempSP | control:NumericWritable | 100.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_207_EF10 |  |  | Setpoints | MinDaTempSP | control:NumericWritable | 60.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_207_EF10 |  |  | Setpoints | CO2LowLvlSP | control:NumericWritable | 400.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_207_EF10 |  |  | Setpoints | CO2HiLvlSP | control:NumericWritable | 1000.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_207_EF10 |  |  | Setpoints | OccClgSP | control:NumericWritable | 74.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_207_EF10 |  |  | Setpoints | UnoccClgSP | control:NumericWritable | 85.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_207_EF10 |  |  | Setpoints | OccHtgSP | control:NumericWritable | 74.00 {overridden} @ 8
Point | BacnetNetwork | MstpTrunk2 | UV_207_EF10 |  |  | Setpoints | UnoccHtgSP | control:NumericWritable | 65.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_207_EF10 |  |  | Setpoints | OaClgEnableSP | control:NumericWritable | 55.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_207_EF10 |  |  | Setpoints | OaHtgEnableSP | control:NumericWritable | 60.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_207_EF10 |  |  | Setpoints | SpaceTempSP | control:NumericWritable | 72.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_207_EF10 |  |  | Setpoints | EconMinPosSP | control:NumericWritable | 0.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_207_EF10 |  |  | Setpoints | NormalOprFanSpdSp | control:EnumWritable | LoSpd {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_207_EF10 |  |  | Setpoints | VRVOprFanSpdSp | control:EnumWritable | HiSpd {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_207_EF10 |  |  | Setpoints | FrzstatLatchReset_OS | kitControl:OneShot | false {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_207_EF10 |  |  | Setpoints | FilterRuntimeRst | control:BooleanWritable | false {ok} @ 10
Point | BacnetNetwork | MstpTrunk2 | UV_207_EF10 |  |  | Setpoints | FilterRuntimeReset_OS | kitControl:OneShot | false {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_207_EF10 |  |  | Setpoints | AllowEconOpr | control:BooleanWritable | false {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_207_EF10 |  |  | Setpoints | Heating_PID_tr | control:NumericWritable | 10.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_207_EF10 |  |  | Setpoints | Heating_PID_maxAo | control:NumericWritable | 0.10 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_207_EF10 |  |  | Setpoints | Heating_PID_minAo | control:NumericWritable | 0.10 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_207_EF10 |  |  | Network | Schedule | control:BooleanWritable | false {ok} @ 16
Point | BacnetNetwork | MstpTrunk2 | UV_207_EF10 |  |  | Network | OaTemp | control:NumericWritable | 58.91 {ok} @ 10
Point | BacnetNetwork | MstpTrunk2 | UV_207_EF10 |  |  | Network | HWSEnable | control:BooleanWritable | true {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_207_EF10 |  |  | Network | TextBlock | baja:WsTextBlock | N/A
Point | BacnetNetwork | MstpTrunk2 | UV_207_EF10 |  |  | Network | OSS | control:BooleanWritable | false {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_207_EF10 |  |  | Network | SetReset | kitControl:BqlExprComponent | false | {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_207_EF10 |  |  | Network | OprModeShare | control:EnumPoint | Fan {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_207_EF10 |  |  | Network | OptStartStop | vykonPro:OptStartStop | N/A
Point | BacnetNetwork | MstpTrunk2 | UV_207_EF10 |  |  | Monitoring | EffOcc | control:BooleanPoint | false {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_207_EF10 |  |  | Monitoring | EffSysEnable | control:BooleanPoint | false {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_207_EF10 |  |  | Monitoring | EffSpaceSp | control:NumericPoint | 74.00 {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_207_EF10 |  |  | Monitoring | FilterMaintenanceAlarm | control:BooleanPoint | false {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_207_EF10 |  |  | Monitoring | EffHeatSP | control:NumericPoint | 65.00 {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_207_EF10 |  |  | Monitoring | EffCoolSP | control:NumericPoint | 85.00 {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_207_EF10 |  |  | EF | EFanSpdSig | control:NumericWritable | 30.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_207_EF10 |  |  | EF | EFanSpdSP | control:NumericWritable | 30.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_207_EF10 |  |  | EF | EFanSts | control:BooleanPoint | false {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_207_EF10 |  |  | EF | EFanCmd | control:BooleanWritable | false {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_207_EF10 |  |  | AV_RandomStartDelay | Proxy Ext | bacnet:BacnetNumericProxyExt | 1.00 | {ok}

## UV_RM208
Type | Network | Trunk | Device | Address | DeviceType | PointFolder | PointName | PointType | Value | Status
Point | BacnetNetwork | MstpTrunk2 | UV_RM208 |  |  | Inputs | DaTemp | control:NumericPoint | 74.95 {unackedAlarm} alarmInhibit
Point | BacnetNetwork | MstpTrunk2 | UV_RM208 |  |  | Inputs | SpaceTemp | control:NumericPoint | 72.30 {unackedAlarm}
Point | BacnetNetwork | MstpTrunk2 | UV_RM208 |  |  | Inputs | SpaceHumidity | control:NumericPoint | 37.97 {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_RM208 |  |  | Inputs | SpaceCO2 | control:NumericPoint | 421.00 {unackedAlarm}
Point | BacnetNetwork | MstpTrunk2 | UV_RM208 |  |  | Inputs | SupplyFanSts | control:BooleanPoint | false {unackedAlarm}
Point | BacnetNetwork | MstpTrunk2 | UV_RM208 |  |  | Inputs | CFSAlm | control:BooleanPoint | false {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_RM208 |  |  | Inputs | GpsSts | control:BooleanPoint | true {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_RM208 |  |  | Inputs | HighAlmSp | kitControl:NumericSwitch | 85.00 {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_RM208 |  |  | Inputs | Add | kitControl:Add | 88.00 {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_RM208 |  |  | Inputs | Subtract | kitControl:Subtract | 62.00 {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_RM208 |  |  | Inputs | SpaceTempAlmEnabOfst | control:NumericWritable | 3.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM208 |  |  | Inputs | SpaceTempAlmDsblDb | control:NumericWritable | 2.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM208 |  |  | Inputs | LowAlmSp | kitControl:NumericSwitch | 65.00 {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_RM208 |  |  | Inputs | Not | kitControl:Not | true {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_RM208 |  |  | Inputs | DaTempHiAlmSp | control:NumericWritable | 100.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM208 |  |  | Inputs | DaTempLoAlmSp | control:NumericWritable | 45.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM208 |  |  | Inputs | DaTempAlmDsblDb | control:NumericWritable | 3.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM208 |  |  | Inputs | DxCallForFan | control:BooleanPoint | false {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_RM208 |  |  | Outputs | SFLowSpdCmd | control:BooleanPoint | false {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_RM208 |  |  | Outputs | SFMedSpdCmd | control:BooleanPoint | false {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_RM208 |  |  | Outputs | SFHiSpdCmd | control:BooleanPoint | false {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_RM208 |  |  | Outputs | VRVEnable | control:BooleanWritable | false {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM208 |  |  | Outputs | SteamVlvSig | control:NumericWritable | 0.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM208 |  |  | Outputs | OaDmprCtrl | control:NumericWritable | 0.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM208 |  |  | Outputs | Or | kitControl:Or | false {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_RM208 |  |  | Overrides | Ov_SpaceTemp | control:NumericWritable | +inf {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM208 |  |  | Overrides | Ov_FanCmd | control:EnumWritable | Auto {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM208 |  |  | Setpoints | DaTempSP | control:NumericWritable | 100.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM208 |  |  | Setpoints | MinDaTempSP | control:NumericWritable | 60.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM208 |  |  | Setpoints | CO2LowLvlSP | control:NumericWritable | 400.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM208 |  |  | Setpoints | CO2HiLvlSP | control:NumericWritable | 1000.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM208 |  |  | Setpoints | OccClgSP | control:NumericWritable | 74.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM208 |  |  | Setpoints | UnoccClgSP | control:NumericWritable | 85.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM208 |  |  | Setpoints | OccHtgSP | control:NumericWritable | 70.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM208 |  |  | Setpoints | UnoccHtgSP | control:NumericWritable | 65.00 {overridden} @ 8
Point | BacnetNetwork | MstpTrunk2 | UV_RM208 |  |  | Setpoints | OaClgEnableSP | control:NumericWritable | 55.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM208 |  |  | Setpoints | OaHtgEnableSP | control:NumericWritable | 60.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM208 |  |  | Setpoints | SpaceTempSP | control:NumericWritable | 72.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM208 |  |  | Setpoints | EconMinPosSP | control:NumericWritable | 0.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM208 |  |  | Setpoints | NormalOprFanSpdSp | control:EnumWritable | LoSpd {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM208 |  |  | Setpoints | VRVOprFanSpdSp | control:EnumWritable | HiSpd {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM208 |  |  | Setpoints | FrzstatLatchReset_OS | kitControl:OneShot | false {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_RM208 |  |  | Setpoints | FilterRuntimeRst | control:BooleanWritable | false {ok} @ 10
Point | BacnetNetwork | MstpTrunk2 | UV_RM208 |  |  | Setpoints | FilterRuntimeReset_OS | kitControl:OneShot | false {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_RM208 |  |  | Setpoints | AllowEconOpr | control:BooleanWritable | false {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM208 |  |  | Setpoints | Heating_PID_tr | control:NumericWritable | 10.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM208 |  |  | Setpoints | Heating_PID_maxAo | control:NumericWritable | 0.10 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM208 |  |  | Setpoints | Heating_PID_minAo | control:NumericWritable | 0.10 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM208 |  |  | Network | Schedule | control:BooleanWritable | false {ok} @ 16
Point | BacnetNetwork | MstpTrunk2 | UV_RM208 |  |  | Network | OaTemp | control:NumericWritable | 58.91 {ok} @ 10
Point | BacnetNetwork | MstpTrunk2 | UV_RM208 |  |  | Network | HWSEnable | control:BooleanWritable | true {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM208 |  |  | Network | TextBlock | baja:WsTextBlock | N/A
Point | BacnetNetwork | MstpTrunk2 | UV_RM208 |  |  | Network | OSS | control:BooleanWritable | false {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | UV_RM208 |  |  | Network | SetReset | kitControl:BqlExprComponent | false | {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_RM208 |  |  | Network | OprModeShare | control:EnumPoint | Fan {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_RM208 |  |  | Network | OptStartStop | vykonPro:OptStartStop | N/A
Point | BacnetNetwork | MstpTrunk2 | UV_RM208 |  |  | Monitoring | EffOcc | control:BooleanPoint | false {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_RM208 |  |  | Monitoring | EffSysEnable | control:BooleanPoint | false {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_RM208 |  |  | Monitoring | EffSpaceSp | control:NumericPoint | 70.00 {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_RM208 |  |  | Monitoring | FilterMaintenanceAlarm | control:BooleanPoint | false {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_RM208 |  |  | Monitoring | EffHeatSP | control:NumericPoint | 65.00 {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_RM208 |  |  | Monitoring | EffCoolSP | control:NumericPoint | 85.00 {ok}
Point | BacnetNetwork | MstpTrunk2 | UV_RM208 |  |  | AV_RandomStartDelay | Proxy Ext | bacnet:BacnetNumericProxyExt | 1.00 | {ok}

## EF4_3_Bathrooms
Type | Network | Trunk | Device | Address | DeviceType | PointFolder | PointName | PointType | Value | Status
Point | BacnetNetwork | MstpTrunk2 | EF4_3_Bathrooms |  |  | Outputs | EF3_Cmd | control:BooleanWritable | true {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | EF4_3_Bathrooms |  |  | Outputs | EF4_Cmd | control:BooleanWritable | true {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | EF4_3_Bathrooms |  |  | Outputs | EF_E_Cmd | control:BooleanWritable | true {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | EF4_3_Bathrooms |  |  | Inputs | EF3_Status | control:BooleanPoint | true {unackedAlarm}
Point | BacnetNetwork | MstpTrunk2 | EF4_3_Bathrooms |  |  | Inputs | EF4_Status | control:BooleanPoint | true {unackedAlarm}
Point | BacnetNetwork | MstpTrunk2 | EF4_3_Bathrooms |  |  | Inputs | EF5_Status | control:BooleanPoint | false {ok}
Point | BacnetNetwork | MstpTrunk2 | EF4_3_Bathrooms |  |  | Inputs | EF6_Status | control:BooleanPoint | false {ok}
Point | BacnetNetwork | MstpTrunk2 | EF4_3_Bathrooms |  |  | Inputs | EF11_Status | control:BooleanPoint | false {ok}
Point | BacnetNetwork | MstpTrunk2 | EF4_3_Bathrooms |  |  | Inputs | EF_E_Status | control:BooleanPoint | ""false {alarm | unackedAlarm}""
Point | BacnetNetwork | MstpTrunk2 | EF4_3_Bathrooms |  |  | Network | EF_Schedule | control:BooleanWritable | true {ok} @ def

## CH_FTR
Type | Network | Trunk | Device | Address | DeviceType | PointFolder | PointName | PointType | Value | Status
Point | BacnetNetwork | MstpTrunk2 | CH_FTR |  |  | Inputs | CH1_SpaceTemp | control:NumericPoint | 74.62 {ok}
Point | BacnetNetwork | MstpTrunk2 | CH_FTR |  |  | Inputs | CH2_SpaceTemp | control:NumericPoint | 73.49 {ok}
Point | BacnetNetwork | MstpTrunk2 | CH_FTR |  |  | Inputs | CH1_2AvgSpaceTemp | control:NumericPoint | 74.06 {ok}
Point | BacnetNetwork | MstpTrunk2 | CH_FTR |  |  | Inputs | EF1_Status | control:BooleanPoint | false {ok}
Point | BacnetNetwork | MstpTrunk2 | CH_FTR |  |  | Inputs | EF2_Status | control:BooleanPoint | false {ok}
Point | BacnetNetwork | MstpTrunk2 | CH_FTR |  |  | Outputs | CH1_Enable | control:BooleanWritable | false {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | CH_FTR |  |  | Outputs | CH2_Enable | control:BooleanWritable | false {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | CH_FTR |  |  | Outputs | FTR_Cafe1 | control:BooleanWritable | false {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | CH_FTR |  |  | Outputs | FTR_Cafe2 | control:BooleanWritable | false {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | CH_FTR |  |  | Outputs | FTR_Cafe3 | control:BooleanWritable | false {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | CH_FTR |  |  | Outputs | FTR_Cafe4 | control:BooleanWritable | false {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | CH_FTR |  |  | Setpoints | RTU_NetOccSpaceSP | control:NumericWritable | 68.00 {ok} @ 10
Point | BacnetNetwork | MstpTrunk2 | CH_FTR |  |  | Setpoints | RTU_NetUnoccSpaceSP | control:NumericWritable | 65.00 {ok} @ 10
Point | BacnetNetwork | MstpTrunk2 | CH_FTR |  |  | Setpoints | CH_OccHeatingSP | control:NumericWritable | 72.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | CH_FTR |  |  | Setpoints | CH_UnoccHeatingSP | control:NumericWritable | 65.00 {ok} @ def
Point | BacnetNetwork | MstpTrunk2 | CH_FTR |  |  | Network | RTU2_NetSpaceTemp | control:NumericWritable | 71.12 {ok} @ 10
Point | BacnetNetwork | MstpTrunk2 | CH_FTR |  |  | Network | RTU3_NetSpaceTemp | control:NumericWritable | 71.62 {ok} @ 10
Point | BacnetNetwork | MstpTrunk2 | CH_FTR |  |  | Network | CH_Schedule | control:BooleanWritable | false {ok} @ 10

## DAIKIN DBACS
Type | Network | Trunk | Device | Address | DeviceType | PointFolder | PointName | PointType | Value | Status
Point | BacnetNetwork | MstpTrunk3 | DAIKIN DBACS |  |  | ACCU1 | Room101 | bacnet:BacnetPointFolder | N/A
Point | BacnetNetwork | MstpTrunk3 | DAIKIN DBACS |  |  | ACCU1 | Room103 | bacnet:BacnetPointFolder | N/A
Point | BacnetNetwork | MstpTrunk3 | DAIKIN DBACS |  |  | ACCU1 | Room201 | bacnet:BacnetPointFolder | N/A
Point | BacnetNetwork | MstpTrunk3 | DAIKIN DBACS |  |  | ACCU1 | Room203 | bacnet:BacnetPointFolder | N/A
Point | BacnetNetwork | MstpTrunk3 | DAIKIN DBACS |  |  | ACCU2 | Room102 | bacnet:BacnetPointFolder | N/A
Point | BacnetNetwork | MstpTrunk3 | DAIKIN DBACS |  |  | ACCU2 | Room104 | bacnet:BacnetPointFolder | N/A
Point | BacnetNetwork | MstpTrunk3 | DAIKIN DBACS |  |  | ACCU2 | Room202 | bacnet:BacnetPointFolder | N/A
Point | BacnetNetwork | MstpTrunk3 | DAIKIN DBACS |  |  | ACCU2 | Room204 | bacnet:BacnetPointFolder | N/A
Point | BacnetNetwork | MstpTrunk3 | DAIKIN DBACS |  |  | ACCU3 | Room105 | bacnet:BacnetPointFolder | N/A
Point | BacnetNetwork | MstpTrunk3 | DAIKIN DBACS |  |  | ACCU3 | Room107 | bacnet:BacnetPointFolder | N/A
Point | BacnetNetwork | MstpTrunk3 | DAIKIN DBACS |  |  | ACCU3 | Room205 | bacnet:BacnetPointFolder | N/A
Point | BacnetNetwork | MstpTrunk3 | DAIKIN DBACS |  |  | ACCU3 | Room207 | bacnet:BacnetPointFolder | N/A
Point | BacnetNetwork | MstpTrunk3 | DAIKIN DBACS |  |  | ACCU4 | Room106 | bacnet:BacnetPointFolder | N/A
Point | BacnetNetwork | MstpTrunk3 | DAIKIN DBACS |  |  | ACCU4 | Room108 | bacnet:BacnetPointFolder | N/A
Point | BacnetNetwork | MstpTrunk3 | DAIKIN DBACS |  |  | ACCU4 | Room206 | bacnet:BacnetPointFolder | N/A
Point | BacnetNetwork | MstpTrunk3 | DAIKIN DBACS |  |  | ACCU4 | Room208 | bacnet:BacnetPointFolder | N/A